## Slide 1: Cryogenic cooling options for radiation testing
Torsten Koettig, Aleksandra Onufrena, Maria Chioteli

## Slide 2: Content
Cooling option comparison T ≥ 4.2 K
Cryocooler based solutions
Remote cooling loops
Summary

## Slide 3: Cooling options/influence on cryostat design
Forced flow or natural circulation,
conduction cooling
Bath cooling,
direct liquid contact
Cryocooler,
conduction cooling
Cryocooler,
remote cooling
Phase separator as cooling source,
conduction cooling
Cryocooler,
ZBO, Vapor condensation
LHe based options
Cryocooler based options

## Slide 4: Cooling options/influence on cryostat design
Forced flow or natural circulation,
conduction cooling
Bath cooling,
direct liquid contact
Cryocooler,
conduction cooling
Cryocooler,
remote cooling
Phase separator as cooling source,
conduction cooling
Cryocooler,
ZBO, Vapor condensation
Liquid transfer lines, return gas active shield cooling
double vacuum insulated
Gas return
LHe based options
Cryocooler based options
LHe supply
He gas lines to the cryocooler, its materials are close to the irradiation region
Possible activation of all internal materials (rare earth alloys)
Radiation hardness of seals?
Reduced lifetime?
=> Pulse tube cryocoolers with He cooling remote circuits
LHe transfer lines in the zone for refill
Cryocooler stand-alone operation

## Slide 5
Cryocooler performance overview

## Slide 6
Cryocooler vs. liquid/vapour cooling
Status Aug. 2024

## Slide 7
Remote cooling circuits => cryocooler based
Gain distance of 1-2 m

## Slide 8
RF cavity cooling in a remote way
Possible fluid conditions
LHe two–phase flow to 6 K
SC He @ 3 bara, 4.5 - 6 K
GHe @ 10 bara, 4.5 - 6 K
GHe @ 20 bara, 4.5 - 6 K
1.8 2.5 4 5 6 8 K

## Slide 9
Remote cooling loop RF cavity cooling
Optimum capillary fluid conditions – numerical code
Similar heat transfer of TPF and Sup. crit. 3 bar
Quite higher pressure drop of TPF

## Slide 10
Supply temperature
Cavity temperature
Additional halogen lamp to mimic uniform heating as expected from RF loads
Heat load introduction to the cavity

## Slide 11: Remote cooling loops with boosted performance
Subcooled 4 bar cooling loop
2 stage
CC
3-4 x
Subcooled 4 bar cooling loop – high Q
2 stage
CC
2 stage
CC
Circulation pump and compressor outside radiation zone
Rad. zone
Rad. zone

## Slide 12
Latest developments (high cooling power at 4.2 K)
Source: Bluefors, Cryomech, Two-stage pulse tube refrigerator, Pel=25-27 kW (50 or 60 Hz)
https://bluefors.com/products/pulse-tube-cryocoolers/pt450/#downloads, photo courtesy Bluefors.

## Slide 13
Latest developments (high cooling power at 4.2 K)
Source: Introduction of GM – JT cooling system, A. Euler, Sumitomo
> 9 W @ 4.2 K cooling power at the CIF
Now also as open ”loop” system available!
Possible add. shield cooler
GM-JT cooler

## Slide 14
Conclusion
Testing radiation hardness of materials at low temperature
LHe cryostats vs. cryocoolers based options
Cooling performance
Pushing the frontier of cryocooler performance => add. J-T circuits
Remote cooling circuits to reduce the amount of materials exposed
New applications for R&D and stand-alone cryostats

## Slide 15
Thank you for your attention