## Slide 2: Introduction to Cryogenics
T. Koettig, P. Borges de Sousa, J. Bremer
Contributions from S. Claudet and Ph. Lebrun
CAS: Basics of Accelerator Physics and Technology, 2025.

## Slide 3: Content
Introduction to cryogenic installations
Motivation => reducing thermal energy in a system
Heat transfer and thermal insulation
Helium cryogenics, He I => He II
Conclusions
References

## Slide 4: Overview of cryogenics at CERN - Detectors
Superconducting coils of LHC detectors @ 4.5 K (ATLAS, CMS)
LAr Calorimeter - LN2 cooled
Different types of cryogens (Helium, Nitrogen and Argon)
From: http://cms.web.cern.ch/news/cms-detector-design
From: CERN-DI-9803026

## Slide 5: Overview of cryogenics at CERN - LHC
Helium at different operating temperatures (thermal shields, beam screens, distribution and magnets,…)
Superconducting (SC) magnets of the LHC ring at T=1.9 K
Accelerating SC cavities at T=4.5 K
CERN CDS-EX-0712013

## Slide 6: Overview of cryogenics at CERN
North area =>
SM18
Antimatter Factory =>
HIE-Isolde
Test facilities =>
Neutrino Platform
…
Sources: CERN-PHOTO-201509-239, CERN-EX-0606017, CERN-PHOTO-201607-170-3, OPEN-PHO-ACCEL-2016-016-7, CERN-PHOTO-201703-077-4

## Slide 7: Cryogenic fluids - Thermophysical properties
Fluid | 4He | N2 | Ar | H2 | O2 | Kr | Ne | Xe | Air | Water
Boiling temperature (K) @ 1.013 bar | 4.2 | 77.3 | 87.3 | 20.3 | 90.2 | 119.8 | 27.1 | 165.1 | 78.8 | 373
Latent heat of evaporation @ Tb in kJ/kg | 20.9 | 199.1 | 163.2 | 448 | 213.1 | 107.7 | 87.2 | 95.6 | 205.2 | 2260
Volume ratio gas(273 K) / liquid | 709 | 652 | 795 | 798 | 808 | 653 | 1356 | 527 | 685 | -----
Volume ratio saturated vapor to liquid (1.013 bar) | 7.5 | 177.0 | 244.8 | 53.9 | 258.7 | 277.5 | 127.6 | 297.7 | 194.9 | 1623.8
Specific mass of liquid (at Tb) – kg/m3 | 125 | 804 | 1400 | 71 | 1140 | 2413 | 1204 | 2942 | 874 | 960

## Slide 8: Cryogenics and Superconductivity

## Slide 9
Characteristic temperatures of low-energy phenomena
Phenomenon | Temperature
Debye temperature of metals | few 100 K
High-temperature superconductors | ~ 100 K
Low-temperature superconductors | ~ 10 K
Intrinsic transport properties of metals | < 10 K
Cryo-pumping | few K
Cosmic microwave background | 2.725 K
Superfluid 4He | < 2.17 K
Bolometers for cosmic radiation | < 1 K
ADR stages, Bose-Einstein condensates | ~ mK

## Slide 10
Alignment targets
LHC main cryostat
(Cross-section)
Multi layer insulation (MLI)
Vacuum vessel
Thermal shield
Magnet support posts (GFRE)
External supports (jacks)
Bottom tray
(50-65 K feed line
~ 19.5 bar)
5-20 K support post
heat intercept
Cryogenic application: Dipole magnets of the LHC
All circuits are cooled by helium
Beam screen

## Slide 11: Heat Transfer and Thermal Insulation

## Slide 12: Cryogenic System Design
Tlow
Refrig.
Thermal insulation
Thigh
Instr. &
Control
Heat load
Structural support
Low temperature environment
Source of refrigeration
Heat exchange strategy
Sample environment
Thermal insulation
Structural support
Instrumentation and control
Vacuum

## Slide 13: Thermal conductivity, solid conduction – how to cool?
Heat transport in solids
Fourier's law:
From: Cryogenie, Institut International du Froid, Paris
Pure dielectric crystals: phonons
Dielectrics/Insulators: phonons
Pure metals: free electron gas and phonons
Alloyed metals: electrons and phonons
(W/m K)
(K)

## Slide 14: Radiative heat transfer – Black body
Source: https://www.researchgate.net/figure/Blackbody-spectral-emissive-power-as-a-function-of-wavelength-for-various-values-of_fig4_320298109
Wien’s law (Maximum of black body power spectrum)
  =>

## Slide 15: Radiative heat transfer – Grey body
Wien’s law (Maximum of black body power spectrum)
  =>
Stefan-Boltzmann’s law
  Black body Qrad = s AT4 s = 5.67 x 10-8 W/(m2 K4)
  (Stefan-Boltzmann’s constant)
  “Grey” body Qrad = e s A T4 e - emissivity of surface
  “Grey” surfaces at T1 and T2 Qrad = E s A (T14 –T24) E - function of e1, e2, geometry
.
.
.

## Slide 16: Emissivity of technical materials at low temperatures
 | Surface at 77 K | Surface at 4.2 K
Stainless steel, as found | 0.34 | 0.12
Stainless steel, mech. polished | 0.12 | 0.07
Stainless steel, electropolished | 0.10 | 0.07
Stainless steel + Al foil | 0.05 | 0.02
Aluminium, as found | 0.12 | 0.07
Aluminium, mech. polished | 0.10 | 0.06
Aluminium, electropolished | 0.08 | 0.04
Copper, as found | 0.12 | 0.06
Copper, mech. polished | 0.06 | 0.02
Condensed layers from gas phase easily vary these values !
From: Ph. Lebrun, CAS School on Vacuum in Accelerators, 2006

## Slide 17: Multi-layer insulation (MLI)
Complex system involving three heat transfer processes
  QMLI = Qradiation + Qsolid + Qresidual
  With n reflective layers of equal emissivity, Qradiation ~ 1/(n+1)
  Parasitic contacts between layers, Qsolid increases with layer density
  Qresidual due to residual gas trapped between layers, scales as 1/n in molecular regime
  Non-linear behavior requires layer-to-layer modeling
Large surface application
Cold surface
Solutions for penetrations and support structures

## Slide 18: Typical heat fluxes between flat plates (cold side vanishingly low)
Configuration | W/m2
Black-body radiation from 293 K | 420
Black-body radiation from 80 K | 2.3
Gas conduction (10-3 mbar He) from 290 K | 19
Gas conduction (10-5 mbar He) from 290 K | 0.19
Gas conduction (10-3 mbar He) from 80 K | 6.8
Gas conduction (10-5 mbar He) from 80 K | 0.07
MLI (30 layers) from 290 K, pressure below 10-5 mbar | 1-1.5
MLI (10 layers) from 80 K, pressure below 10-5 mbar | 0.05
MLI (10 layers) from 80 K, pressure 10-3 mbar | 1-2

## Slide 19: Refrigeration and Liquefaction

## Slide 20
300
10
5
2
Thermodynamics of cryogenic refrigeration
He @ 4.5 K ec=65.7 => 1/COP 230
H2 @ 20 K ec=14
N2 @ 77 K ec=2.9
Graph for Twarm = 300 K
For low temperatures ec=
Use of low temperatures if no alternative
Better intercept heat at higher temperatures
He @ 1.8 K ec=166 => 1/COP 980

## Slide 21: Elementary cooling processes in a T-s diagram
p1
p2 < p1
isobaric

## Slide 22
Maximum Joule-Thomson inversion temperatures
p/bar
Source: http://faculty.chem.queensu.ca/people/faculty/mombourquette/
Chem221/3_FirstLaw/ChangeFunctions.asp

## Slide 23
Maximum Joule-Thomson inversion temperatures
Cryogen | Max. inversion temperature [K]
Helium | 43
Hydrogen | 202
Neon | 260
Air | 603
Nitrogen | 623
Argon | 723
Air can be cooled down and liquefied by J-T expansion from room temperature,
Helium and hydrogen need precooling down to below the inversion temperature by heat exchange or work-extracting expansion (e.g. in turbines)
p/bar
Source: Refprop® NIST
Source: http://faculty.chem.queensu.ca/people/faculty/mombourquette/
Chem221/3_FirstLaw/ChangeFunctions.asp

## Slide 24: Combining all three processes in a cryoplant
p1
p2 < p1
isobaric

## Slide 25: Claude cycle ( Turbo Brayton + JT )
Temperature 
Specific entropy s 
HEX
Turbin
expan.
HEX
JT
Source: Frey, Haefer, Tieftemperaturtechnologie, VDI Verlag 1981, ISBN 3-18-400503-8, adapted.

## Slide 26
Process diagram, LHC refrigerator 18 kW @ 4.5 K
Heat exchangers
Turbines
Adsorbers (remove impurities)
LN2 (cool-down)

## Slide 27
COP of large cryogenic helium refrigerators
Size of the plant matters
Tokamak
in France
e+e- Accel.
in Japan
Heavy ion
collider US
LINAC ring
US
Circular acc.
Germany
e+e- Accel.
CERN
Hadron Acc.
CERN
1/COP Wel/Wcryo @ 4.5 K

## Slide 28
LHC 18 kW @ 4.5 K helium cryoplants
Th. shields: 33 kW @ 50 K to 75 K
Beam screen: 23 kW @ 4.6 K to 20 K
Current leads: 41 g/s liquefaction
4 MW compressor power
1/COP 220-230 Wel/W @ 4.5 K
Air Liquide
Linde

## Slide 29
LHC 18 kW @ 4.5 K helium cryoplants
33 kW @ 50 K to 75 K
23 kW @ 4.6 K to 20 K
41 g/s liquefaction
4 MW compressor power
COP 220-230 W/W @ 4.5 K
Air Liquide
Linde
8 x 18 kW @ 4.5 K
1800 SC magnets
36,000 ton @ 1.9 K
96 ton of He
24 km and 20 kW @ 1.9 K

## Slide 30
Pressure (kPa)
From Weisend, Handbook of
Cryogenic Engineering, 1984.
4He phase diagram
Helium has no triple point
Solid He only above 25 bar
Lambda line => He I / He II separ.
He II with very special properties

## Slide 31
LHC Cooling scheme
Header B
VLP pumping
Header C
4.6 K, 3 bara
Header D
20 K return
Header F
Shield return
Current leads return
Source: adapted from CERN, LHC design report, ch. 11
SC cavities are cooled in a 4.5 K saturated LHe bath
Main supply
E
From
From

## Slide 32: Cryogenic Fluid Properties He I and He II

## Slide 33: From He I to He II
Normal fluid helium => He I
    Like a standard fluid: viscosity etc.
Superfluid helium => He II
  Temperature < 2.17 K
  Peak in heat capacity cp at Tλ
  Very high thermal conductivity
  Low / vanishing viscosity
Murakami, Experimental study of thermo-fluid dynamic effect in He II cavitating flow, Cryogenics, 2012.

## Slide 34
Phase Boundary
Phase diagram of 4He
From Weisend, Handbook of
Cryogenic Engineering, 1984.
Tλ ≈2.1768 K @
pλ ≈ 50.41 mbar

## Slide 35
Glass cryostat set-up
LN2
LHe
Vacuum
insulation
Transfer line
From Ekin, Experimental Techniques for Low Temperature Measurements, 2006.
Vacuum
pump
Pumping
Boiling in He I
Boiling suddenly
stops in He II

## Slide 36
Boiling effects during cooldown / Pumping on the He vapour

## Slide 37
How to explain that unique behaviour ?
Two fluid model of L. Tisza:
He II is composed of two components

## Slide 38
Two-fluid model of He II by Tisza, 1938
Formal description of He II as the sum of a normal and a superfluid component.
Ratio ρs/ρn depends on temperature
Superfluid component:
no entropy: Ss = 0
zero viscosity: ηs = 0
Normal component:
carries total entropy: Sn = S
finite viscosity: ηn = ηn
From Gross, Marx, Wather-Meissner Institut, 2009.
Temperature / K
ρs/ρ, ρn/ρ

## Slide 39: He II in practice

## Slide 40
Superleak below Tl
1963 movie by Alfred Leitner, Michigan State University

## Slide 41
Critical heat flux in He II
He II level
Power supply
Heater
Cryostat
Heat and mass flow are
limited by a critical velocity:
v > vcr
Superfluid behavior becomes
non-linear (mutual friction)
k and η
Formation of vapor bubbles at
the surface of the heater
In He II re-condensation of
the vapor
Surface tension let the bubbles
implode
Implosion speed exceeds v1
Shock wave => cavitation

## Slide 42
Critical heat flux in He II (T<Tl)

## Slide 43
LHe I cooling (T>Tl)

## Slide 44: Concluding remarks
Cryogenics serving superconducting systems is now part of all major accelerators and future projects.
While advanced applications tend to favour “T< 2 K”, many almost industrial applications are based on “4.5 K” and R&D continues for “high temperature” applications.
Reducing the amount of required helium as cooling fluid is essential for future installations.
Even though cryogenic engineering follows well defined rules and standards, there are still variants depending on boundary conditions, project schedule …
I could only recommend that demonstrated experience is evaluated and adapted to specific requirements you may have.

## Slide 45: Some references
K. Mendelssohn, The quest for absolute zero, McGraw Hill (1966)
R.B. Scott, Cryogenic engineering, Van Nostrand, Princeton (1959)
G.G. Haselden, Cryogenic fundamentals, Academic Press, London (1971)
R.A. Barron, Cryogenic systems, Oxford University Press, New York (1985)
B.A. Hands, Cryogenic engineering, Academic Press, London (1986)
S.W. van Sciver, Helium cryogenics, Plenum Press, New York (1986)
K.D. Timmerhaus & T.M. Flynn, Cryogenic process engineering, Plenum Press, New York (1989)
Proceedings of CAS School on Superconductivity and Cryogenics for Particle Accelerators and Detectors, Erice (2002)
  U. Wagner, Refrigeration
  G. Vandoni, Heat transfer
  Ph. Lebrun, Design of a cryostat for superconducting accelerator magnet
  Ph. Lebrun & L. Tavian, The technology of superfluid helium
Proceedings of ICEC and CEC/ICMC conferences
CERN, HSE, Cryogenic Safety courses 1-3

## Slide 46: Thank you for your attention.

## Slide 48
Spare slides

## Slide 49: Superconductivity
H. Kamerlingh Onnes
Liquefied helium in 1909 at 4.2 K with 60 g He inventory
Observed in 1911 for the first time superconductivity of mercury
Nobel prize 1913
Historic graph showing the superconducting transition of mercury, measured in Leiden in 1911 by H. Kamerlingh Onnes.

## Slide 50: Heat capacity of materials – what to cool?
Source: Enss, Low temperature physics.
Metals have a contribution of free electron gas => dominant at very low temperature
Source: Ekin, Experimental Techniques for Low-Temperature Measurements.
Discrete lattice vibrations => Phonons

## Slide 51: Emissivity of technical materials at low temperatures
 | Cold surface, 77 K | Gas inlet
1 | Al + Cat-a-Lac | Uniform over time, 0.06 Pa
2 | Ni + Black Velvet 101-C10/3M | Sporadic
3 | Ni + Black Velvet 101-C10/3M | Uniform over time, 0.1 Pa
4 | Al, polished, ε = 0.07 | Uniform over time, 0.06 Pa
5 | Ni, polished | Sporadic
6 | Ni, polished | Uniform over time, 0.1 Pa
Emissivity ε
Layer thickness d
Emissivity of cold surface coated with water condensate dependent on layer thickness
Source: Haefer, Kryovakuumtechnik, 1981

## Slide 52
Thermodynamics of cryogenic refrigeration
First principle [Joule]
Second principle [Clausius]
(= for reversible process)
Hence,
which can be written in different ways:
Carnot factor
introducing entropy S as

## Slide 53
Tsink = 1.85 K
Tload_max = 1.9 K
LHC cryogenic distribution scheme - QRL
37’500 tons at 1.9 K
Pressurized/saturated He II
Qdist = 450 W
Qload = 2400 W
Source: Ph. Lebrun, Cooling with Superfluid Helium

## Slide 54
The effectiveness of J-T expansion
Source: Ph. Lebrun, Cooling with Superfluid Helium

## Slide 55
Refrigerator Liquefier

## Slide 56
Refrigerator Liquefier
For refrigerators/liquefiers with the same efficiency:

## Slide 57
Energy consumption CERN, LHC and Cryo
CERN in total is around 200 MW with LHC contributing by 115 MW
Source: https://www.lhc-closer.es/taking_a_closer_look _at_lhc/0.energy_consumption
When the LHC is up and running the total average power for the whole CERN site will peak during July at about 180 MW of which:
  LHC cryogenics 27.5 MW (40 MW installed)
  LHC experiments 22 MW
1.25 TWh in 2018