## Slide 1
Commissioning of the cryogenic system of the HL-LHC Inner Triplet (IT) String without magnets and next steps
214th TE Technical Meeting (TE-TM)
4 November 2024
A. Onufrena, A. Perin, A. Lees, O. Pirotte, J. Gery, T. Colin, R. Mauny, M. Pezzetti, T. Barbe, A. Tovar, N. Guillotin, D. Valencon, N. Trikoupis, V. Gahier, T. Dupont, all the Cryogenics and WP16 Teams
https://indico.cern.ch/event/1470595/
WP16

## Slide 2
Introduction and cryogenic infrastructure of IT String
Overview of commissioning phases
Main commissioning results
  Cold compressor
  Heat loads and pressure drop on the lines
  Estimated cooling capacity
Next steps and conclusions
Outline

## Slide 3
SM18 hall
For the High Luminosity LHC (HL-LHC) project, the final focusing Inner Triplet (IT) superconducting magnets around ATLAS and CMS will be replaced by a new 60 m-long set of higher performance Nb3Sn magnets
IT String test facility: consists of all magnet circuits from D1 to Q1 and cold powering with their respective systems (cryogenics, quench protection, …)
Key objectives
Validate collective behaviour of the magnets & their systems in the conditions as similar as possible to the operational ones
Obtain information about the operational behaviour in advance to speed up the commissioning in the LHC tunnel
D1
Q2b
CP
Q3
Q2a
Q1
Introduction

## Slide 4
60 m-long cryogenic distribution line (SQXL)
Cold compressor
(CCU)
Warm quench buffer (WQB)
Warm pumping units (WPUs)
IT magnets area
PCDS (70 m)
Specific to the IT String
SQXL: cryogenic distribution line
PCDS: proximity cryogenic distribution system
CC: cold compressor
WQB: warm quench buffer
Gas management system of DFHX
Data acquisition & control system
Part of SM18 infrastructure
Warm quench buffer
Existing refrigerator
Warm pumping units
Main helium storage
Cryogenic architecture for HL-LHC IT String in SM18
Quench line
TL05
Gas management panel
Warm Quench Buffer
2 x 15 kW heaters
Number if items/assemblies tracked : >1000
Instrumentation: 376 items with 190 not in magnets & cold powering
Thermometers : 227 with 81 not in mag. & cold powering
Valves : 185 total, 31 cryogenic
SQXL
Refrigerator

## Slide 5
Cryogenic system was under design and construction from 2020 and underwent three commissioning runs in 2023-2024
Tendering and construction
Today
Cryogenic system was built and ready for commissioning in 2023
Three commissioning runs
Project overview
Planned start of commissioning with magnets in 2025

## Slide 6
Introduction and cryogenic infrastructure of IT String
Overview of commissioning phases
Main commissioning results
  Cold compressor
  Heat loads and pressure drop on the lines
  Estimated cooling capacity
Next steps and conclusions
Outline

## Slide 7
Jun 2023 (and before)
Jul-Aug 2023
Aug-Oct 2023
Nov 2023
Dec 2023
Jan-Apr 2023
May 2023
Jun 2023
Jul - Oct 2024
Heat load in TL01, contacts and repair
Phase 1b
Phase 1c
IT String commissioning phases
  Phase 1a
  Controlled cooldown
  Mechanical integrity validation
  Heat load on some segments is higher than expected
Repair of the cold compressor (CCU)
System ready for the cooldown
  Phase 1b (further validation and studies):
  System thermal characterization (heat loads, pressure drop)
  X-ray inspection of TL01 line at cold
  Further tuning of control loops and CCU logic test
  Phase 1c (additional studies):
  CCU logic validation
  TL01 repair validation and capacity measurements
Cryogenics operating team
  Phase 1: commissioning of the cryogenic system without magnets (complete!)
  Phase 2: commissioning (and then operation) of the cryogenic system with magnets (2nd half of 2025)
Strategy: commission the cryogenic system in a standalone mode before operation with magnets (allows to anticipate and resolve any potential issues)

## Slide 8
Requirements and operating parameters of the cryogenic system
Parameter | Value
Static heat load (conduction and radiation) on all cold masses at 1.9 K | 135 W
Dynamic heat load (magnetisation during a nominal current ramp and splice resistance) on cold masses at 1.9 K | 201 W
Magnet cold mass temperature | 1.9 K
Nominal magnet current and ramp rate | 16.2 kA @ 14.6 A/s
Screen temperature | 50 K-75 K
Mass flow for cold powering system | 6 g/s
Max. allowed along the magnets | 30 K
Max. allowed within thermal radiation shields | 100 K
Maximum cooldown duration | 15 days
Parameter | Value
Static heat load (conduction and radiation) on all cold masses at 1.9 K | 135 W
Dynamic heat load (magnetisation during a nominal current ramp and splice resistance) on cold masses at 1.9 K | 201 W
Magnet cold mass temperature | 1.9 K
Nominal magnet current and ramp rate | 16.2 kA @ 14.6 A/s
Screen temperature | 50 K-75 K
Mass flow for cold powering system | 6 g/s
 | 30 K
 | 100 K
Maximum cooldown duration | 15 days
336 W of heat load at 1.9 K
Operating requirements for IT String (derived from HL-LHC)
drives the cooldown speed

## Slide 9
Requirements and operating parameters of the cryogenic system
Goal: validate that these conditions can be achieved by the cryogenic system
Parameter | Value
Static heat load (conduction and radiation) on all cold masses at 1.9 K | 135 W
Dynamic heat load (magnetisation during a nominal current ramp and splice resistance) on cold masses at 1.9 K | 201 W
Magnet cold mass temperature | 1.9 K
Nominal magnet current and ramp rate | 16.2 kA @ 14.6 A/s
Screen temperature | 50 K-75 K
Mass flow for cold powering system | 6 g/s
Max. allowed along the magnets | 30 K
Max. allowed within thermal radiation shields | 100 K
Maximum cooldown duration | 15 days
Parameter | Value
Static heat load (conduction and radiation) on all cold masses at 1.9 K | 135 W
Dynamic heat load (magnetisation during a nominal current ramp and splice resistance) on cold masses at 1.9 K | 201 W
Magnet cold mass temperature | 1.9 K
Nominal magnet current and ramp rate | 16.2 kA @ 14.6 A/s
Screen temperature | 50 K-75 K
Mass flow for cold powering system | 6 g/s
 | 30 K
 | 100 K
Maximum cooldown duration | 15 days
336 W of heat load at 1.9 K
drives the cooldown speed
 |  |  | Nominal |  | Cooldown / warm-up | 
Header | Function | [K] | [bar] | [g/s] | [bar] | [g/s]
B | Line with He II at 16 mbar /1.8-1.9 K | 1.9 | 0.016 | 18 | < 1 | 1
C | He supply | 4.6 | 3.2 | 26 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 1.3 | 2 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23 | 15 | 23
F |  | 75 | 15 | 23 | 14 | 23
 |  |  | Nominal |  | Cooldown / warm-up | 
Header | Function |  |  |  |  | 
B | Line with He II at 16 mbar /1.8-1.9 K | 1.9 | 0.016 | 18 | < 1 | 1
C | He supply | 4.6 | 3.2 | 26 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 1.3 | 2 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23 | 15 | 23
F |  | 75 | 15 | 23 | 14 | 23
Flows, temperatures and pressures in the headers during the commissioning
Operating requirements for IT String (derived from HL-LHC)

## Slide 10
IT String flow scheme for standalone commissioning
Cold Box (CB)
Phase separator
Bypass
Future IT magnets
Caps

## Slide 11
Phase separator
Caps
Bypass
Cold compressor (CCU)
Warm pumps (WPU)
Cryogenic distribution line (SQXL)
Proximity cryogenics (PCDS)
Cold Box (CB)
IT String flow scheme for standalone commissioning

## Slide 12
Cooldown: 300 K → 4.5 K / 1.8 K (Line B)
Phase separator
14 bar → 1.3 bar
15 bar → 3 bar
Line | Function | [K] | [bar] | [g/s]
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Line | Function |  |  | 
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Nominal conditions in the headers

## Slide 13
Cooldown: 300 K → 4.5 K / 1.8 K (Line B)
Phase separator
14 bar → 1.3 bar
15 bar
14 bar
15 bar → 3 bar
Line | Function | [K] | [bar] | [g/s]
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Line | Function |  |  | 
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Nominal conditions in the headers

## Slide 14
Cooldown: 300 K → 4.5 K / 1.8 K (Line B)
Phase separator
14 bar → 1.3 bar
15 bar
14 bar
1 bar → 16 mbar
15 bar → 3 bar
Line | Function | [K] | [bar] | [g/s]
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Line | Function |  |  | 
B | He II at 16 mbar /1.8-1.9 K | 1.9 | 1 → 0.016 | 1
C | He supply | 4.6 | 15 → 3.2 | < 100
D | LP return / quench | 20 | 14 → 1.3 | < 100
E | Shield lines | 50 | 15 | 23
F |  | 75 | 14 | 23
Nominal conditions in the headers

## Slide 15
Introduction and cryogenic infrastructure of IT String
Overview of commissioning phases
Main commissioning results
  Cold compressor
  Heat loads and pressure drop on the lines
  Estimated cooling capacity
Next steps and conclusions
Outline

## Slide 16
Cold compressor logic validation
System is equipped with a cold compressor unit (CCU) to allow for a lower pressure (and ) in line B
CCU is a centrifugal compression machine, may be subject to stall-surge during operation (especially in transient modes)
Special control sequence was developed and CCU was tested in transient and nominal regimes
Results: sequence was validated, developed logic was able to ensure operation in the stable (1h) and transient regimes (temperature and heat load variation, quench-like pressure rises) within stall-surge limits
Lower
Higher
Nominal operation
Examples of CCU operation curves on its performance map
1 → Start (𝑚 ̇ corresponds to static 𝑄 ̇ of the magnets + SC-link) & thermalisation
1-2 → Start the CCU which controls the pressure in line B
2-3 → Transient: pre-loading of the magnets
3-4 → Ramp / nominal operation
4-5 → Deceleration and controlled stop
Chart: Operating sequence of CCU
| 0 | 10 | 20 | 60 | 70 | 80
m | 14 | 14 | 24 | 24 | 14 | 14
m_IT | 8 | 8 | 18 | 18 | 8 | 8
m_link | 6 | 6 | 6 | 6 | 6 | 6
p | 12 | 10 | 10 | 10 | 10 | 12
Chart: Operating sequence of CCU
| 0 | 10 | 20 | 60 | 70 | 80
m | 14 | 14 | 24 | 24 | 14 | 14
m_IT | 8 | 8 | 18 | 18 | 8 | 8
m_link | 6 | 6 | 6 | 6 | 6 | 6
p | 12 | 10 | 10 | 10 | 10 | 12
Total [g/s]
Pressure in line B [mbar]
in magnets [g/s]
in SC-link [g/s]
1
2
3
4
5
CCU head during re-integration

## Slide 17
60 m-long cryogenic distribution line (SQXL)
IT magnets area
PCDS (70 m)
TL05
SQXL
6 kW refrigerator
Pressure drop and heat loads
Pressure drops and heat loads of distribution system consisting of proximity cryogenics (PCDS) and cryo distribution line (SQXL) were measured
was measured using absolute pressure sensors with prior x-calibration
and measurement methods:
Lines TL01 / TL02 / TL03

## Slide 18
Magnet temperature analysis:
Worst case scenario: test results transfer into 17.5 mbar and 1.82 K inside the bayonet HX during nominal operation → margin for operation (0.3 K below -point)
Pressure drop
Challenge: large system with low & absolute pressure sensors (offset-calibration before each measurement)
Critical lines
Line D ( affects helium release after quench): pressure drop in line with predictions, no abnormality observed
Line B (pumping, defines the lowest for saturated helium → magnet ):
Bayonet HX (Line B to pumps)
Cross-section of IT magnet
Magnet bath at 1.3 bar (Line D to quench buffer)
Warm Quench Buffer
 | [g/s] | [K] | [mbar] | Total [mbar] | 
 |  |  |  | Predicted | Test
Line B | 18 | 2.4 | 13.6 | 4.1 | 5.00.2
 |  |  |  | Predicted | Test
Line B | 18 | 2.4 | 13.6 | 4.1 | 
Result: measured pressure drop is in line with predicted values and compatible with operations

## Slide 19
Heat loads
on Line D inside TL02 is higher than expected
 | Proximity cryogenics (PCDS), length 70 m |  |  |  | Cryo distribution line (SQXL), length 60 m |  |  | Total (PCDS+SQXL), length 130 m |  | 
 | TL01 Line C | TL02 Line D | TL03 Line B | TL05 Lines C/D/B | Line C | Line D | Line B | Line C | Line D | Line B
Predicted [W] | 7 | 13 | 9 | 10/10/10 | 9 | 33 | 15 | 26 | 56 | 34
Measured [W] | 6 | 83 | < 9 | 15/5/7 | 29 | 60 | 12 | 50 | 148 | 28
Error [%] | 20 | 15 | 34 | 22/22/29 | 23 | 16 | 24 | 18 | 14 | 22
 | TL01 Line C | TL02 Line D | TL03 Line B | TL05 Lines C/D/B | Line C | Line D | Line B | Line C | Line D | Line B
Predicted [W] | 7 | 13 | 9 | 10/10/10 | 9 | 33 | 15 | 26 | 56 | 34
Measured [W] | 6 | 83 | < 9 | 15/5/7 | 29 | 60 | 12 | 50 | 148 | 28
Error [%] | 20 | 15 | 34 | 22/22/29 | 23 | 16 | 24 | 18 | 14 | 22
Potential reasons for observed :
Conduction / radiation from warm vacuum barriers (not the case during operation with magnets)
Other sources: improperly mounted MLI & design issues (under investigation)
  Ice on TL02 (Line D)
Measured on Lines B / C(PCDS) / TL05 are in line with predictions
TL01 repair reduced the heat load by 6-16 W
Bent spacer inside TL02
Line C
Vacuum barrier
Control Valve
Piping
Effect of warm vacuum barriers

## Slide 20
Results
Cooling capacity (after TL01 repair): 6 g/s (cold powering) + 310 W (magnets) at 1.8 K
With the measured in Line B, the current ramp will start at 1.8 K → magnets will drift in by less than 0.1 K during the ramp and remain at around 1.9 K during ramp & nominal operation
Capacity tests
Goal: validate that the cryogenic system can provide sufficient cooling for the magnets
Highest heat dissipation during 19-minute nominal magnet ramp (14.6 A/s): 135 W (static) + 201 W (dynamic) → 336 W
Capacity tests: nominal fluid conditions during the ramp → cooling power can be calculated from temperatures in Line C
Conclusion: cryogenic system has a sufficient cooling capacity to keep the magnets at 1.9 K during nominal operation

## Slide 21
Introduction
Cryogenic infrastructure of IT String
Overview of commissioning phases
Main commissioning results
  Cold compressor
  Heat loads and pressure drop on the lines
  Estimated cooling capacity
Next steps and conclusions
Outline

## Slide 22
Magnets planned to be in place by Mar 2025 and commissioning with magnets is planned for Q3-Q4 of 2025 → aim to have the cryogenic system ready by May 2025
Next steps: planning for 2025
Today
Phase 1a
Phase 1b
Phase 1c
Target to be ready by end of May 2025
Planned start of commissioning with magnets in Q3-Q4 2025

## Slide 23
Mechanical activities
SQXL jumper preparation for magnet connection is on-going
  Q2a arrived and D1 jumper open (TE-MSC)
  D1 installation planned this week
Connection of cold powering:
  Gas management system (GMS) installed
  Warm recovery line (WRL) constructed and connected to GMS
  GMS to be connected to DFHX (WP6a)
Warm quench buffer connection
  Design / preparation for fabrication of connection are on-going
  Connection is planned for Mar-Apr 2025
Mechanical consolidations following commissioning without magnets (TL02, valve checks) are on-going
Quench buffer
TL02
Next steps: preparation of commissioning with magnets
Connection of WRL
Connection of bayonet from DFHX
Open D1 jumper
Installation of Q2a
Gas management system (GMS) for cold powering
Installed warm recovery line (WRL)

## Slide 24
Electrical activities
Cabling of the magnet & cold powering instrumentation
  Rack side: GMS and DFHX connection is in progress
  IT String side (magnet and DFHX): connections are in preparation
H5 diagnostics and installation of HL-LHC-like CPU (on-going)
Fast acquisition and data acquisition validation
Instrumentation consolidations following commissioning
Preparation for commissioning with magnets
Preparation of test procedures and documentation
  IT String commissioning document (sequences, functional specification)
  NCRs (TL01 completed, TL02 in preparation)
Control logic and analysis tools (to be defined and programmed)
Review of interfaces with other systems (vacuum, quench protection)
Next steps: preparation of commissioning with magnets
Control logic to be defined

## Slide 25
Cryogenic system for IT String has been built and commissioned in a standalone mode (without magnets and cold powering)
Mechanical integrity and functionality of instrumentation were validated
IT String cooldown procedure was validated, and nominal conditions were achieved in all lines
Heat loads and pressure drop measured (system characterization) → higher heat loads than expected on Lines C/D
The cryogenic system has a sufficient cooling capacity to keep the magnets at 1.9 K → system has been validated for the IT String operation
Activities in preparation for commissioning with magnets (Phase 2) are on-going
Conclusions

## Slide 27
Mass flows rate:
  Mass flow meters (e.g. Coriolis) installed on some lines
  Four additional methods to determine :
    Using the position and flow coefficient of a control valve ()
    Using an in-flow heater and across it
    Using a heater immersed in liquid helium and the latent heat of evaporation
    Using the inlet pressure of the volumetric WPU
Heat loads: measurement methods and challenges
Temperature: sensors (pipe elements and in-flow sensors) located along the lines were used for evaluation
In-flow sensor in Line B
Pipe elements on Lines C/E/F
Heater (EH)
Isenthalpic expansion in CV
Isenthalpic expansion in CV
Challenges: high uncertainties at low , low near peak for Line C, stratification of supercritical fluid at low , radiation shield drift during tests at low