## Slide 1: P8 SEU mitigation measures on cryo system for 2025 and 2026 LHC physics Run (and LS3). M. Pezzetti with the material of B. Ivent, B. Bradu, F. Morant & L. Delprat
AMB

## Slide 2: QURCA P8 US85 / UL84 (elevator exit)
QURCA
AMB-Mecos

## Slide 3: AMB location today and HEH fluence (2024)
AMB MECOS (Active Magnetic Bearings of cold compressors) are located today at the UL84 right extremity (US85 side)
MECOS AMB radiation sensitivity = one failure each 108 HEH/cm2 (data obtained after radiation tests in HiRadMat)
Fluka simulations in 2020 were indicating a fluence of ~5.107 HEH/cm2 at this location for an integrated lumi in LHCb of 10 fm-1
AMB4 is the most exposed electronic device (but AMB 1,2,3 are also at risk !)
CC1
CC2
CC3
CC4
Courtesy of A. Ciccotelli,
F. Cerutti - EN/STI/BMI (2020)
AMB
High Energy Hadron (HEH) fluence for 10 fm-1 accumulated in LHCb with Run3 config

## Slide 4: ΦHEH, no wall / ΦHEH, wall at Different Heights
y = 0 m ± 1.1 m
y = 7 m ± 1.1 m
y = 3 m ± 1.1 m
y = 10 m ± 1.1 m
Poor shielding effect exactly where one
of the most radiation exposed rack is located!

## Slide 5: Electronic Rack at UL84 Entrance - HEH Fluence
y = 0 m ± 1.1 m
Rack position
HEH fluence z-profile averaged within the electronic rack
Current rack center position
2 meters shift towards the UL84
The region where the rack is located showcases a steep gradient in HEH fluence
Moving the rack by a few meters could lead to a significant decrease in its radiation exposure!
HEH fluence averaged within the rack drastically decreases from 7.5 ∙ 107 to 2.4 ∙ 107 cm-2 / 50 fb-1 shifting it towards the UL84 by 2 meters
Such a shift leads to a factor ∼ 3 drop of the mean HEH fluence within the rack!

## Slide 6: Electronic Rack at UL84 Entrance - HEH Fluence - Current Layout
y = 0 m ± 1.1 m
Rack position
HEH fluence z-profile averaged within the rack
Current rack center position
50 cm shift
towards the UL84
50 cm shift towards the UL84 ⟶ Factor ~ 1.6 drop in the mean HEH fluence within the rack
60 cm shift towards the UL84 ⟶ Factor ~ 1.8 drop in the mean HEH fluence within the rack
Reduction factor z-profile averaged within the rack
The region where the rack is exhibits an even steeper gradient in HEH fluence under the current configuration compared to conditions with a potential shielding wall in place:
An even greater impact is expected by shifting the rack towards the UL84
2024 layout -
No Shielding Walls
50 cm shift
towards the UL84
Current rack center position

## Slide 7: UL84 moving “Step by step”
AMB
~ 50- 60 cm moving !
1. ECR – TE-CRG
2. IMPACT – TE-CRG
3. Coordination/Integration – EN-ACE
4. Electrical Lock out – TE-CRG
5. Structure adaptation (Cutting) – EN-ACE
6. Blocking factors : assess cables length – TE-CRG
7. Moving – Transport
8. Recommissioning – TE-CRG
https://panoramas.cern.ch/viewer?fov=16.00&id=55665551&lat=-32.92&lon=176.50

## Slide 8
AMB
UL84 (elevator exit)
AMB

## Slide 9: And……

## Slide 10: LS3 “QURCA-8-EMC01” cabinet relocation
AMB
Wall (of iron block) installation & relocation of QURCA-8-EMC01
Wall (of iron block)
QURCA-8-EMC01
EN/EL cabling necessary (minor but essential)