## Slide 1
Forum on Tracking Detector Mechanics 2025 Bristol, UK
Lorenzo Bistoni, EP-CMX-ID
With major contributions from: D. Abbaneo, G. Baldinelli, P. F. Cianchetta. On behalf of the CMS Tracker Group
Experimental tests on TBPX cooling loops at different CO2 vapour qualities

## Slide 2
Longitudinal layout of the upgraded CMS Tracker
TBPS
TEDD
TB2S
TBPX
TFPX
TEPX
Vapour Quality (VQ):
Heat flux [kW/m^2]
Thermal runaway (Tα):
α
Tα
VQ Target = 42%
Validated with extensive tests on Outer Tracker Structures
Introduction
Detector | Inner Diameter [mm] | Max Heat Flux [kW/m^2]
TBPX | 1.6 | 50
TFPX | 2.5 | 18
TEPX | 2.1 | 19
TBPS tilted | 2.2 | 8
TBPS Flat | 2.0 | 16
TB2S | 2.0 | 5
TEDD | 2.2 | 5

## Slide 3
A
B
C
D
E
REF | OBJECT | Material | Inner Diameter [mm] | Outer Diameter [mm]
A,E | Transfer line | Titanium | 2.8 | 3.2
B,D | Transfer line | Stainless Steel | 2.5 | 3
C | Evaporator | Stainless Steel | 1.6 | 1.8
Lyon Cold Room – CERN B.186
TRACI: CO2 bi-phase cooling plant.
PT1000: Temperature reading
Thermal paste
Test setup

## Slide 4
Cooling loops: current design TBPX PH2
4 different cooling loops, restrictions due to pipe lengths
Cooling loop | HF [kW/m2] | VQ multiline | Power [W] | Flow test [g/s]
Z+ L3-1 | 50 | 38% | 126 | 1.2
Z+L3-9/ Z+ L3-10/ Z- L4-1/ Z- L4-2 | 50 | 40% | 126 | 1.2
Z+ L3-2 | 39 | 39% | 94 | 0.9
Z- L2-8 | 30 | 37% | 73 | 0.8
Nominal conditions
Max heat fluxes of TBPX
Further evaluations
50 [kW/m^2]: Different Vapour Quality tested, from 20% to 50%.
Reducing flow with fixed power
40%, 33%, 25% : Different Heat Fluxes tested, from 5 to 60 kW/m^2
Changing both flow & power
1 Hz sampling frequency
~10 minutes per case
Test plan

## Slide 5
In designed operating conditions, TBPX loops shows consistent temperature instabilities
Instabilities since DAY 1 of tracker!
Why..?
11
12
13
14
2
4
5
6
7
8
9
10
1
3
Results: temperature over time. 50 kW/m^2, different VQ

## Slide 6
Probably because:
(courtesy P. Petagna)
When the size of the bubbles reaches dimensions comparable to the pipe ID, they cannot evolve freely, and the possible boiling patterns are different: “confined flow”
Hypothesis

## Slide 7
Test campaign: different VQ (40 %, 33%, 25%) and HF (5 to 60 kW/m^2)
Complete thermal test results: https://indico.cern.ch/e/1528650
Main points:
VQ at 40%: First spikes at 40 kW/m^2
VQ at 33%: First spikes at 50 kW/m^2
VQ at 25%: Stable temperature for all Heat fluxes!
25% of VQ as a new operation parameter for TBPX
More mass flow needed!
Can we push more flow?
Pressure drop constraint
Thermal runaway constraint
New evaluation of both flow rate and capillaries (diameter and lengths): Multiline simulations
17/06/2025
Results

## Slide 8
Fixed parameters:
Tpoint16 = -35deg [B]
dPpoints5-16 = 10 bar [AB]
B
A
Service channel transfer lines
Bulkhead transfer lines
Manifold on bulkheads
Capillaries
Pre-heaters
On-detector supply pipe
Evaporators
Minifittings
On-detector return pipe
Return jumper
0.8m-2m
Depends on sub-detector
Lengths depends on sub detector
17/06/2025
Boundary condition for new calculations

## Slide 9
Chart: dP capillaries [bar] TBPX Z+, Z-
| Z+ L1-1 | Z+ L2-1 | Z+ L2-2 | Z+ L3-1 | Z+ L3-2 | Z+ L4-1 | Z+ L4-2 | Z+ L1-4 | Z+ L2-6 | Z+ L3-8 | Z+ L3-9 | Z+ L3-10 | Z+ L4-7 | Z+ L4-8 | Z- L1-1 | Z- L2-1 | Z- L2-2 | Z-L3-1 | Z- L4-1 | Z- L4-2 | Z- L4-3 | Z- L1-4 | Z- L2-7 | Z- L2-8 | Z-L3-5 | Z- L3-6 | Z- L4-9 | Z- L4-10
ΔP cap VQ25% | 8.6732 | 8.9464 | 9.0059 | 9.1239 | 9.33 | 8.1059 | 8.4437 | 9.0466 | 8.5671 | 8.3131 | 9.1139 | 9.0906 | 8.8901 | 8.1496 | 8.9266 | 8.503 | 8.7207 | 8.3257 | 9.1285 | 9.1677 | 7.6459 | 9.3152 | 9.0866 | 9.4629 | 8.8631 | 8.0858 | 8.3327 | 7.4018
ΔP cap VQ33% | 9.0334 | 9.2995 | 9.3435 | 9.4175 | 9.566 | 8.5241 | 8.7708 | 9.2912 | 8.8658 | 8.6087 | 9.3403 | 9.326 | 9.1677 | 8.513 | 9.2216 | 8.8479 | 8.9983 | 8.7033 | 9.3598 | 9.391 | 7.9978 | 9.4777 | 9.3165 | 9.5982 | 9.1414 | 8.4598 | 8.615 | 7.9716
ΔP cap VQ42% | 9.1683 | 9.3241 | 9.4451 | 9.4748 | 9.6021 | 8.7602 | 8.895 | 9.4561 | 9.1344 | 8.9616 | 9.497 | 9.4851 | 9.3575 | 8.833 | 9.3125 | 9.0859 | 9.2352 | 8.7706 | 9.5069 | 9.5322 | 8.4994 | 9.5945 | 9.4873 | 9.6913 | 9.3813 | 8.7006 | 8.9101 | 8.2763
ΔP tot
ΔP evap
ΔP capillaries 8 bars guaranteed in mostly all the loops, even at VQ 25%
Reducing VQ = increasing the flow
Is the flow still balanced?
17/06/2025
Pressure drop:
Notes: Se mettiamo più flusso nell’evaporatore, la sua Perdita di pressione sarà più alta e, quindi quella del capillare più bassa. Teniamo dappertutto 8 bar?

## Slide 10
VQ 25% Z- L4-10
VQ 40% Z- L4-10
More ΔP in the evaporator = higher inlet temperature
Constraints on thermal runaway...
17/06/2025
ΔP effect on CO2 temperatures [°C] in the evaporator:

## Slide 11
Chart: 
| Z+ L1-1 | Z+ L2-1 | Z+ L2-2 | Z+ L3-1 | Z+ L3-2 | Z+ L4-1 | Z+ L4-2 | Z+ L1-4 | Z+ L2-6 | Z+ L3-8 | Z+ L3-9 | Z+ L3-10 | Z+ L4-7 | Z+ L4-8 | Z- L1-1 | Z- L2-1 | Z- L2-2 | Z-L3-1 | Z- L4-1 | Z- L4-2 | Z- L4-3 | Z- L1-4 | Z- L2-7 | Z- L2-8 | Z-L3-5 | Z- L3-6 | Z- L4-9 | Z- L4-10
Tmax_evap VQ25% [°C] | -32.1237 | -32.7246 | -32.8633 | -33.1206 | -33.5741 | -31.0596 | -31.777 | -32.9579 | -31.8262 | -31.5044 | -33.0988 | -33.0606 | -32.5621 | -31.1577 | -32.6977 | -31.676 | -32.1754 | -31.5472 | -33.1115 | -33.1949 | -30.1002 | -33.526 | -32.9887 | -33.831 | -32.5102 | -31.0586 | -31.6438 | -29.7009
Tmax_evap VQ33% [°C] | -32.6922 | -33.2903 | -33.3901 | -33.5812 | -33.9152 | -31.8395 | -32.3767 | -33.4432 | -32.4819 | -32.145 | -33.5623 | -33.5432 | -33.1527 | -31.9226 | -33.2947 | -32.4696 | -32.7764 | -32.3717 | -33.5872 | -33.6523 | -30.7967 | -33.8449 | -33.4552 | -34.0928 | -33.1028 | -31.8395 | -32.264 | -30.7432
Tmax_evap VQ42% [°C] | -33.1634 | -33.4928 | -33.7525 | -33.8246 | -34.0984 | -32.4542 | -32.7546 | -33.777 | -33.0777 | -32.894 | -33.8677 | -33.8512 | -33.5373 | -32.6162 | -33.4774 | -32.926 | -33.2661 | -32.5143 | -33.8773 | -33.9304 | -31.8633 | -34.0763 | -33.8091 | -34.2754 | -33.5675 | -32.3627 | -32.8507 | -31.366
Less VQ = More ΔP = Higher Tin [°C]
VQ [%]
Tmax[°C]
17/06/2025
Tmax CO2 evaporators, TBPX Z+, Z-

## Slide 12
Chart: 
| Z+ L1-1 | Z+ L2-1 | Z+ L2-2 | Z+ L3-1 | Z+ L3-2 | Z+ L4-1 | Z+ L4-2 | Z+ L1-4 | Z+ L2-6 | Z+ L3-8 | Z+ L3-9 | Z+ L3-10 | Z+ L4-7 | Z+ L4-8 | Z- L1-1 | Z- L2-1 | Z- L2-2 | Z-L3-1 | Z- L4-1 | Z- L4-2 | Z- L4-3 | Z- L1-4 | Z- L2-7 | Z- L2-8 | Z-L3-5 | Z- L3-6 | Z- L4-9 | Z- L4-10
Thermal Runaway Margin (K) VQ25% | 10.1237 | 4.5246 | 4.6633 | 3.9206 | 4.3741 | 5.4596 | 6.177 | 10.9579 | 3.6262 | 2.3044 | 3.8988 | 3.8606 | 6.9621 | 5.5577 | 10.6977 | 3.476 | 3.9754 | 2.3472 | 7.5115 | 7.5949 | 4.5002 | 11.526 | 4.7887 | 5.631 | 3.3102 | 1.8586 | 6.0438 | 4.1009
Thermal Runaway Margin (K) VQ33% | 10.6922 | 5.0903 | 5.1901 | 4.3812 | 4.7152 | 6.2395 | 6.7767 | 11.4432 | 4.2819 | 2.945 | 4.3623 | 4.3432 | 7.5527 | 6.3226 | 11.2947 | 4.2696 | 4.5764 | 3.1717 | 7.9872 | 8.0523 | 5.1967 | 11.8449 | 5.2552 | 5.8928 | 3.9028 | 2.6395 | 6.664 | 5.1432
Thermal Runaway Margin (K) VQ42% | 11.1634 | 5.2928 | 5.5525 | 4.6246 | 4.8984 | 6.8542 | 7.1546 | 11.777 | 4.8777 | 3.694 | 4.6677 | 4.6512 | 7.9373 | 7.0162 | 11.4774 | 4.726 | 5.0661 | 3.3143 | 8.2773 | 8.3304 | 6.2633 | 12.0763 | 5.6091 | 6.0754 | 4.3675 | 3.1627 | 7.2507 | 5.766
Reduction in vapour quality
More ΔP in the evaporator
Higher inlet temperature
Smaller thermal runaway margin
The minimum margin is 1.86°C in Z- L3-6 with 25% VQ. (1.3°C lower than VQ 42%)
17/06/2025
NB: T.R. margin are evaluated for different integrated luminosity:
2000 fb-1 for L1
4000 fb-1 for L2,L3,L4
Thermal runaway margins (Tα – Tmax)

## Slide 13
High temperature instabilities: behaviour close to dryout or prolongated contact pipe-bubbles
  No way of accepting this instabilities: they will occour from day 1 of future tracker!
Original design: ID = 1.6 mm, max HF = 50kW/m^2, VQ = 42%
Worst Therm. Runaway margin is 2.98 [°C]
All cooling loops guarantee ΔPcapillaries > 8 bar
No instabilities detected during our tests
TBPX current design: ID = 1.6 mm, max HF = 50kW/m^2, VQ = 25%
Worst Therm. Runaway margin is [1.86°C]
Mostly all cooling loops guarantee ΔP capillaries > 8 bar
17/06/2025
Conclusions

## Slide 14
Thanks for your attention
Questions?
17/06/2025
lorenzo.bistoni@cern.ch
Forum on Tracking Detector Mechanics 2025 Bristol, UK
- Lorenzo Bistoni, EP-CMX-ID
With major contributions from: Duccio Abbaneo, Giorgio Baldinelli, Pier Filippo Cianchetta. On behalf of the CMS Tracker Group

## Slide 15
Test | Length [m] | Surface [m2] | Power [W] | HF [kW/m2] | Flow [g/s] | VQ multiline | P_PH [W] | HP th [W] | P_PH + HP th[W] | HP Test [W] | Flow test [g/s]
Z+ L3-1 | 0.50 | 0.00251 | 126.10 | 50.30 | 1.20 | 0.38 | 8.00 | 6.46 | 14.46 | 20 | 1.21
Z+L3-9/ Z+ L3-10/ Z- L4-1/ Z- L4-2 | 0.50 | 0.00251 | 126.10 | 50.30 | 1.14 | 0.40 | 8.00 | 6.46 | 14.46 | 20 | 1.15
Z+ L3-2 | 0.50 | 0.00250 | 94.58 | 37.88 | 0.92 | 0.39 | 8.00 | 6.50 | 14.46 | 20 | 0.93
Z- L2-8 | 0.48 | 0.00242 | 72.90 | 30.17 | 0.75 | 0.37 | 8.00 | 6.52 | 14.46 | 20 | 0.79
Cooling loops: current design TBPX ph2
50 kW/m^2, different VQ[%]:
VQ[%] | Power [W] | Ftest [g/s]
0.50 | 126.4 | 0.92
0.45 | 126.4 | 1.02
0.42 | 126.4 | 1.10
0.40 | 126.4 | 1.15
0.38 | 126.4 | 1.21
0.35 | 126.4 | 1.32
0.33 | 126.4 | 1.40
0.30 | 126.4 | 1.54
0.28 | 126.4 | 1.65
0.25 | 126.4 | 1.84
0.20 | 126.4 | 2.29
40 % VQ, different HF:
HF [kW/m2] | Power [W] | Ftest [g/s]
60 | 150.42 | 1.37
55 | 137.88 | 1.25
50 | 126.10 | 1.17
45 | 112.81 | 1.07
40 | 100.28 | 0.95
35 | 87.74 | 0.88
30 | 75.21 | 0.79
25 | 62.67 | 0.67
20 | 50.14 | 0.57
15 | 37.60 | 0.46
10 | 25.07 | 0.37
5 | 12.53 | 0.26
33 % VQ, different HF:
HF [kW/m2] | Power [W] | Ftest [g/s]
60 | 150.42 | 1.66
55 | 137.88 | 1.51
50 | 125.35 | 1.42
45 | 112.81 | 1.30
40 | 100.28 | 1.15
35 | 87.74 | 1.06
30 | 75.21 | 0.95
25 | 62.67 | 0.81
20 | 50.14 | 0.69
15 | 37.60 | 0.79
10 | 25.07 | 0.68
5 | 12.53 | 0.55
25 % VQ, different HF:
HF [kW/m2] | Power [W] | Ftest [g/s]
60 | 150.42 | 2.19
55 | 137.88 | 2.00
50 | 125.35 | 1.88
45 | 112.81 | 1.71
40 | 100.28 | 1.52
35 | 87.74 | 1.40
30 | 75.21 | 1.26
25 | 62.67 | 1.06
20 | 50.14 | 0.91
15 | 37.60 | 1.04
10 | 25.07 | 0.89
5 | 12.53 | 0.73
Backup: full test plan
17/06/2025

## Slide 16
50 kW/m^2 different vapour qualities:
1
2
3
4
5
6
7
8
9
10
11
12
13
14
Cooling loops:
ΔT from average ≃ 60°C for higher H.F.
Instabilities also at lower ones
different vapour qualities:
ΔT from average > 10°C between 30 % and 33% VQ
Cooling loops:
Backup: Results: temperature over time, cooling loops and 50 kW/m^2
17/06/2025

## Slide 17
Test | HF [kW/m2]
Z+ L3-1 | 50.30
Z+L3-9 | 50.30
Z+ L3-2 | 37.88
Z- L2-8 | 30.17
Test | VQ
Z+ L3-1 | 0.38
Z+L3-9 | 0.40
Z+ L3-2 | 0.39
Z- L2-8 | 0.37
Backup: Results: AVG & STD loops
17/06/2025

## Slide 18
Backup: Results: AVG & STD 50 kW/m^2
17/06/2025

## Slide 19
40% VQ:
Significant instabilities for HF ≥ 40kW/m^2
Backup: Results: temperature over time 40%VQ
17/06/2025

## Slide 20
Backup: Results: AVG & STD 40%VQ
17/06/2025

## Slide 21
1
2
3
4
5
6
7
8
9
10
11
12
13
14
25% & 33% VQ, small heat fluxes:
Small spikes detected at 33%, 20 and 25 kW/m^2
Backup: temperature over time 33% & 25% VQ
17/06/2025

## Slide 22
1
2
3
4
5
6
7
8
9
10
11
12
13
14
25% & 33% VQ, high heat fluxes:
Spikes detected at high HF for 33% of VQ, no spikes at 25% VQ
Backup: temperature over time 33% & 25% VQ
17/06/2025

## Slide 23
Backup: AVG & STD 33%
17/06/2025

## Slide 24
Backup: AVG & STD 25% VQ
17/06/2025

## Slide 25
12.3
1: Reliably in subcooling
1’: Saturation at T1 temperature
0 : Starting point
A : Saturation point at T0 Temp.
0: P_in is measured, surely saturated.
0 – 1 : We create a striction with an outlet valve. In 1 we were in saturated condition. Hypotesys that 1-1’ is isothermic
1’: x = 0, T = -31.2°C
A: p = 12.3 bar, h = 124 j/g
0:
p = 12.3 bar
h = 130.77 J/g
x = 2.212 %
F: 1.083 g/s
x =0.022
Dh at 12.3 bar = 311.9 J/g
W = F*x*Dh
W =7 watt
h = 130.77 J/g
Backup: heat pickup
17/06/2025

## Slide 26
Pt1000 -Embedded sensors
Preheater
PT1000
=
=
= 9W
= 4 W
Tin_bph
Tin_box
Tout_box
Tair
Tair_box
Backup: heat pickup
17/06/2025