## Slide 1: Overview krypton project Forum on Tracking Detector Mechanics 2025 University of Bristol, UK.
Luca Contiero PhD student NTNU-CERN June 19th, 2025

## Slide 2: Content
Introduction
  Why krypton as cooling agent?
New cycle technology
  Principle
  Ejector as passive pumping device
  Experimental assessment
  Installation at CERN
Potential applications
  Low temperature cooling (-40/-80 °C)
  Ultra-low temperature (ULT) cooling (< -80°C)
Future program
  Oil-free machine development
  HTC & Δp performance map
Conclusion

## Slide 3: Fluid study analysis: why krypton?
Low-mass detectors demand:
  Integration of small cooling channels (hardware minimization)
  Uniform temperature distribution
The working temperature range allows to select potential candidates  Critical pressure and temperature
Krypton
Old cooling choice at CERN
Improved performance near critical point
Assess the dependence of the change in saturation temperature on pressure drop
Krypton appears to have better thermal performance at small pipe diameters
VHTC =
{ T = -80°C, Q = 200 W, L = 2 m, VQ = 0-35% }

## Slide 4: New cycle technology: p-h diagram
Starting conditions in gas-phase precludes the use of pumped loop system (2PACL)
Room temperature
Starting point
CO2 limit
New technology must be developed to avoid thermal shocks on the detector modules  CONTROLLED COOLDOWN
This challenges apply to any potential coolant for ULT, as fluids with low critical temperature are required for boosted performance
Similar pressure levels to CO2

## Slide 5: New cycle technology: Ejector-driven system
Pumping loop driven by the ejector
Vapor compression cycle
System must be oil-free
Layout of the detector loop partially unaltered with respect to 2PACL
Use of an ejector as pumping device
External high-pressure (accumulator) tank for single-phase operation & transition to two-phase

## Slide 6: New cycle technology: Two-phase operation
Ejector sucks liquid
Gas compression (no risk of sending liquid)
Capillary
Vaporization in the detector
Rejection to CO2 primary
Expansion primary flow
Local depressurization invoke flow to the detector (p < pout,det)
Free-compression

## Slide 7: New cycle technology: Ejector
Mechanical devices involving no moving parts and widely applied to transcritical CO2 systems
Devices for high-pressure control
They utilize energy from a high-pressure flow to entrain and compress a low-pressure stream
They can work with gas, liquids, two-phase and solid
Comprise three main parts: motive nozzle, mixing chamber and diffuser
No risk of liquid delivered to the compressor due to flooded operation in the detector
It works as the pump in the 2PACL!
But how to regulate the pumping capacity?
Adjust pressure motive (primary) flow
Have multiple static ejectors in parallel
(see Danfoss https://www.danfoss.com/en/products/dcs/valves/electric-
expansion-valves/multi-ejector-solution/)
Adjust nozzle throat area by inserting a needle (see Carel https://www.carel.com/emj-electronic-modulating-ejector)

## Slide 8: New cycle technology: Experimental prototype
Compressor and detector mockup box built at NTNU (Norway)
Use of an oil-lubricated transcritical CO2 compressor with standard oil
Initially coupled with Julabo chiller for testing main transients (startup, cooldown, two-phase)
Missing external high-pressure tank and cold primary CO2 chiller  system is now moved at CERN
Ejector

## Slide 9: New cycle technology: startup
  Ejector loop is decoupled from vapor compression cycle at the start
  High-pressure control and connection to the bladder allows to avoid thermal shocks all time at the start
  Compressor starts and thermally stabilize
  Ejector opens to start circulating gas through the detector
  V.10 is initially used to add additional degree of controllability
accumulator
accumulator
Closed

## Slide 10: New cycle technology: startup

## Slide 11: New cycle technology: cooldown
  The cooldown is driven by the external chiller, which provides additional cooling to the high-pressure side of the krypton system
  Ejector and valves in the detector loop are used to adjust the cooldown speed
  Average cooldown speed of ≈ 2 K/min

## Slide 12: Installation of the prototype at CERN
Connection to a primary CO2 chiller (system A)
External tank (bladder accumulator) is used to provide an isobaric cooldown when the system is in gas/supercritical phase
It provides additional refrigerant charge as the CO₂ primary circuit progressively cools down the krypton
In the prototype nitrogen is used for the pressurization, however small diffusion towards the krypton side may occur
  In the real system, a pneumatic accumulator with no interface among the two fluids must be used
Bladder accumulator
Krypton bottle
N2 bottle
Refrigeration system

## Slide 13: Installation of the prototype at CERN
The system is currently not in operation due to some hardware issues:
Delay from the company
Defected connector of the bladder
Leak during
pressure test
Bladder has been dismounted and soon a technician from the company will reseal the bladder

## Slide 14: Potential application for krypton cooling
For the low-temperature cooling, different approaches are under investigation depending on what is required by the detectors:
Use of supecritical krypton to provide cooling below the CO2 triple point
  In this respect studies conducted by PhD Camila Pedano will serve as fluid-to-fluid scaling (ScCO2 to ScKr)
  Operation with fluid in single-state
  Optimal temperature range (with respect to possible isothermal operation) is within -50 to -62°C
Nearly isothermal cooling can be achieved by proper designing the cooling lines

## Slide 15: Potential application for krypton cooling
For the low temperature cooling (-30 < T < -55°C):
As the ejector system works with both CO2 and krypton, another option is to run the cycle with CO2 to reach temperatures unattainable by the 2PACL
  A primary chiller is no longer needed as a multi-stage CO2 system can reject heat directly to the air
  CO2 system can now potentially reach temperatures down to -53°C
  A configuration with two interchangeable parallel systems provides the flexibility to switch to krypton as working fluid if colder temperatures will be required (in opposition to use directly supercritical krypton)
Only illustrative example!
Intercooling
First stage compression
Second stage compression
Capillary
Detector
Liquid circulation driven by ejector
Current 2PACL limit (-40°C)
Rejection to H2O - air
CO2

## Slide 16: Potential application for krypton cooling
For the ultra-low cooling, ≈ -100°C and below, krypton can be an alternative coolant for future detectors at HL-LHC using Silicon Photomultipliers (SiPM) with single photon detection capabolity:
This detector technology has almost no power to be dissipated, future upgrade will required extremely cold cooling down to -140°C
Currently a cryogenic system is under investigation but the same krypton system, although with few different requirements (almost no thermal load, i.e. recirculation of mainly liquid via the ejector), can potentially be used:
  It allows integration of small cooling pipes
  With one single system the thermal loads coming from the surrounding structure and cables can easily be evacuated

## Slide 17: Future work
The cycle technology developed gave promising results, now the focus is on:
Demonstration of the real detector cooling system coupled with a CO2 primary chiller and the external high-pressure tank
Extensive test on supercritical and two-phase operation
A new PhD (Lukas Köster) has started in Norway aiming to:
  Study heat transfer and pressure drop performance of krypton in minichannels
  Development of an oil-free compressor, in this respect:
    It is of primary importance for the success of the development to involve an industrial partner
    Few industrial partners have shown their interest in taking part of the project
    While the development of the system is covered by CERN & NTNU funding, the compressor development is lacking an economic support

## Slide 18: Thank you for your attention!
Contributors of the project: Luca CONTIERO(a,b), Bart VERLAAT(a), Paolo PETAGNA(a), Armin HAFNER(b), Krzysztof BANASIAK(b), Yosr ALLOUCHE(b),
CERN, Geneva, 1211, Switzerland, luca.contiero@cern.ch
NTNU, Trondheim, 7491, Norway