## Slide 2: Target Systems ventilation system integration 1st Beam Dump Facility (BDF) Targetry Systems Advisory Committee (TSAC)
F.Dragoni, N.Zaric
05/03/2025
https://hiecn3.web.cern.ch

## Slide 3: Agenda
Review of confinement consumptions in ventilation systems
  Reference documents
New service building
  Ventilation systems & pressure cascade
  Preliminary failure modes and impacts
Underground area
  Ventilation systems
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 4: New service building – ventilation system
RP input document: EDMS 3237086
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 5: New service building – ventilation system
RP input document: EDMS 3237086
  Class A requirements: - min. fresh air: 5 ach - min. ΔP: -50Pa - extraction must be guaranteed in case of power cut  Redundant power supply
  Class C requirements: - no min. fresh air requirements - needs for underpressure level, but no min. requirements - no needs for redundant power supply
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 6: New service building – ventilation system
FIRIA input document: EDMS 3237086
  Fire compartments
  Smoke extraction zones
  Filtration needed for CLASS A (service cell)
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 7: New service building – ventilation system
FIRIA input document: NANOLAB example
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 8: New service building – ventilation system
S-1 Zone
Full fresh air ~ 2,300 m3/h
N+1 redundancy
Filters nearby Service Cell and in filter room
S-2 Zone
Full fresh air ~ 12,660 m3/h
No redundancy
Filters in filter room
S-3 Zone
~ 1,000 m3/h
No redundancy
-20Pa
0Pa
0Pa
0Pa
0Pa
+30Pa
-30Pa
-10Pa
-50Pa
-10Pa
-10Pa
-10Pa
-10Pa
-30Pa
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 9: New service building – ventilation synoptics
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 10: New service building – ventilation synoptics
Service Cell
  2,300 m3/h full fresh air supply unit
  Extractor rated at 400 ̊C /2h +  maintenance of -50 Pa as required  this system will be on Redundant power supply
  Two level of exhaust air filtration
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025
(Smoke) extractors
1st level of filtration
2nd level of filtration
Fresh air intake
AHUs
S-1 supply

## Slide 11: New service building – ventilation synoptics
ALL OTHER ROOMS except Control room
  12,660 m3/h full fresh air unit
  Recirculation of air possible for some rooms  using less energy for treating fresh air
  Smoke extraction for some zones, extractors rated at 400 ̊C /2h
  One level of exhaust air filtration
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025
Smoke extractors
Filters
Fresh air intake
AHU
Smoke extraction system
S-2 supply
S-2 return
Extractors
S-2 exhaust

## Slide 12: New service building – ventilation synoptics
Control room
  1,000 m3/h unit
  Recirculation of air  using less energy for treating fresh air
  No needs for mechanical smoke extraction
  Only fresh air is filtrated
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025
AHU
Fresh air intake
S-3 supply
S-3 return

## Slide 13: New service building – ventilation ductwork and integration
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025
Groundfloor
1st floor
2nd floor

## Slide 14: New service building – ventilation ductwork and integration
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025
S-2 AHU
S-3 AHU
S-1 AHUs
Filters
Smoke extractors

## Slide 15: New service building – ventilation ductwork and integration
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 16: Demineralized & Chilled water synoptics
New service building: 250 kW load on chilled water for AHUs
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 17: New service building – ventilation system
SERVICE CELL
Preliminary failure modes and impacts – Service cell
AHU
AHU
DYNAMIC CONFINEMENT
HANDLING HALL
DOOR
REDUNTANT POWER SUPPLY
EXTRACTOR
EXTRACTOR
New service building – ventilation system
POWER CUT
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 18: New service building – ventilation system
ROOMS
Preliminary failure modes and impacts – ALL OTHER ROOMS except Control room
AHU
DYNAMIC CONFINEMENT
BLD.911
DOOR (4m x 5.5m)
EXTRACTOR
EXTRACTOR
New service building – ventilation system
POWER CUT
SMOKE EXTRACTOR
SMOKE EXTRACTOR
REDUNTANT POWER SUPPLY
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 19: New service building – ventilation system
CONTROL ROOM
Preliminary failure modes and impacts – Control room
AHU
DYNAMIC CONFINEMENT
New service building – ventilation system
POWER CUT
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 20: Underground cavern – TCC8 & ECN3
  ECN3: Cooling capacity: 125kW Flow rate: 30.000m3/h
  TCC8: Cooling capacity: 168kW Flow rate: 20.000m3/h
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 21: Underground cavern – TCC8 & ECN3
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025

## Slide 22: Underground cavern – TCC8
Fire rated smoke extraction ducts, up to 240 min
Class “D” leakage rate ducts
Extractors will be placed on the roof of service building
F. Dragoni, N. Zaric | Target Systems ventilation system integration
4-6 March 2025