## Slide 1: Cold Powering System for HL-LHC
Y. Leclercq, C. Barth, A. Ballarino G. Willering & V. Gahier
on behalf of WP6a and all collaborators
TE-TM meeting 13.01.2025

## Slide 2: Motivation : HL-LHC Cold Powering
SCLinkM
DFHM
DFM
DFX
SCLinkX
DFHX
IP 
Power Converters
Power Converters
IT magnets
MS magnets
20 K
60 K
300 K
4.5 K
20 K
60 K
300 K
Triplets (X):
74.5 m long
117 kA DC
Matching Sections (M):
120 m long
40 kA DC
4.5 K
8 (+2 spares) Systems required
Two types :
  X for Triplets
  M for Matching Sections
3 cryostats in series per system :
  DFX-SCLinkX-DFHX
  DFM-SCLinkM-DFHM
Temperature range 4.5 K to 300 K
3 superconductors types
  Nb-Ti
  MgB2
  REBCO
Service Galleries UR
LHC tunnel
HL-LHC layout: IT & MS magnets powered with power converters located in new galleries 50 metres away
Cold Powering Key Function: Electrical connection between magnets in LHC tunnel and power converters in service gallery

## Slide 3: Overview of the IT Cold Powering system
NbTi-NbTi
splices
NbTi-MgB2 splices
DFX
SCLink
DFHX
Splice
Splice
To IT magnets
To PC
Superfluid
Helium : 1.9K
Liquid
Helium : 4.5K
Gaseous Helium
Electrical
19 branches from 2 to 18 kA
Total rated up to |117| kA DC
Nb-Ti busbars through λ-Plate & DFX
  Immersed in Lhe @ 4.5 K
MgB2 cable from DFX to DFHX
  In gaseous mass flow < 20 K
REBCO cables : DFHX to Current leads
  Cable & splices convective cooled < 60 K
Cryogenics
DFX liquid helium bath ≈ 400 l
200 W Heaters in DFX produce a controlled gaseous mass flow through SCLink
Mass flow adapted to current leads needs
MgB2 & REBCO cables and splices convective cooled
Current leads convective cooled
Electrical
Heater
Gas flow
< 20K
< 60K
300 K

## Slide 4: Cold Powering System : Assembly of SCLink+DFHX
10 months assembly duration
Various electromechanical activities : welding, handling, splicing, forming, adjusting, QC
Flex cryostat Unspooling
MgB2 Cable Shuffling
Cryostats connections
Cable insertion
Shuffling box welding
High current cryostat assembly
Cold mass structure assembly
2 kA CL assembly
2 kA MgB2-REBCO splices

## Slide 5: Cold Powering System : Assembly of SCLink+DFHX
18 kA CL assembly
18 kA MgB2-REBCO splices
Ancillaries
Cold mass closure
Vacuum vessel closure
Quality Controls
SCLink+DFH assembly

## Slide 6: Cold Powering System : Connection to F2 test bench
DFX end assembly
Cryogenic & electrical connections
MgB2-Nb-Ti connections
Electrical shortcuts
SCLink forming
DFX assembly
DFX connection to F2
DFHX connection to F2
Quality Controls

## Slide 7
SM18 facility : new dedicated F2 bench
Liquid helium injected in DFX, recovered at 300 K at DFHX end
Electrical powering from DFHX, electrical shortcuts at DFX end
Cold Powering System test bench
LHe
DFX
Superconducting Link
DFHX
GHe recovery
Powering 18 kA, 15 kA, 2 kA, 2 kA

## Slide 8
DFX : MLI installation leading to colder surfaces
Cool-Down:
To nominal cryogenic conditions < 1 week
Mass flow < 3.0 g/s
300K to 100K : TDFHX-TDFX <50K then 70K
< 100K, injection of LHe
Cryostats performance:
General
  No condensation
  Mass flow production in DFX validated up to 10 g/s
  10 min nominal conditions maintained in case of Liquid helium supply stop : confirmed
DFX static heat loads : 67 W, +30W extra heat loads due to MLI installation, no impact on operation
SCLink linear heat load : 2.0 W/m
DFHX : no cold point, no measurable pressure drop up to splices, splices convective cooling
Cold Test : Cryogenics performances

## Slide 9: Cold Test : Thermal Contractions
Waves with regular fixed points to allow movement
Two thermal cycles (RT  cryogenic conditions) followed by powering of all circuits
Repetitive performance with local displacement < 30 mm.
F = Fixed Point
Movements
(up to 3 cm)

## Slide 10: Cold Test : Powering Scheme
+ & - of each circuit in shorted @ 4.2 K
Similar circuits connected in series @ RT
Four power converters:
18 kA: Inominal = 16.23 kA (MQXF)
15 kA: Inominal = 12.11 kA (Dipole)
2 kA: Inominal = 2 kA (Trim)
2 kA: Inominal = 1.74 kA (Correctors)
Maximum current delivered by the power converters: 94 kA

## Slide 11: Cold Test : Flow & Temperatures
Within specifications:
  79.2 kA (Inominal of HL-LHC magnets) @ 5.5 g/s
Avg. current lead:
  gHe flow: 50 mg·s-1· kA-1
REBCO cable splice & lead temp. stable
Splice temp. limit: 25 K
Lead temp. setpoints:
  18 kA: 50 K
  15 kA: 55 K
  2 kA: 50 – 60 K
1st full X-type Cold Powering System successfully cold tested:
Transported 94 kA @ 5.0 g/s gHe flow

## Slide 12: Cold Test : Superconductors cables
15 / 18 kA circuits: MgB2 cables
15 / 18 kA circuits: REBCO cables + lower lead HEX
UMgB
2
75 m
*QD threshold: 5 mV
MgB2
cable
REBCO cables
lower lead HEX
current lead
RT terminal
Usplice
UREBCO+ lower HEX
Stable, no transition, x10 – x100 below QD threshold*

## Slide 13: Cold Test : Splices
Stable, Tsplice independent of current ( 1 K)
REBCO to MgB2, GHe @ 20 K
MgB2 to Nb-Ti, LHe @ 4.5 K
Nb-Ti to Nb-Ti, LHe @ 4.5 K
U: 15 / 18 kA circuits: REBCO to MgB2
T: 15 / 18 kA circuits: REBCO to MgB2

## Slide 14: Cold Test : High Voltage
HV tests successfully passed, NOC leakage x100 below limit
*accepted leakage current: ≤ 10 µA
At nominal operating conditions & warm gHe
HV between all circuit combinations and PE

## Slide 15: Cold Test : Transient behavior & Handling
Transient behaviour validated:
  Circuit cross-talk (< 50 µH coupling) allowing 100 A/s ramps
  Quenches of 2 kA - Corrector circuits do not trigger QD of any of the other circuits
    Very low inductance (0.03 µH) due to coaxial layout
Handling of Cold Powering Systems validated:
Spooling & transportability (incl. crane) demonstrated
Circuit | Test current (kA) | Ramp rate (A/s) | Inductive coupling (µH) |  |  | 
 |  |  | 18 kA | 15 kA | 2 kA - Trim | 2 kA - Correctors
18 kA | 18 | 100 | 31.0* | 8.1 | 15.0 | 2.3
15 kA | 15 | 100 | 0.1 | 0.1* | 18.0 | 0.03
2 kA - Trim | 2 |  |  |  | * | 
2 kA - Correctors | 2 | 50 | 0.03 | 0.03 | 0.02 | 1.5*
*self inductance

## Slide 16
The first Cold Powering System for the HL-LHC Triplets has been successfully validated:
  Cryogenic, electrical and mechanical performance all met design parameters
  Robustness of system in different operating modes was proven
The system transferred 94 kA* in DC mode with 5.0 g/s gHe:
  MgB2 @ 20 K (Operation of MgB2 cable possible up to 29 K)
  REBCO cables @ 60 K (Operation of REBCO cables possible up to 70 K)
    10 K temperature margin
Spooling & transportability (incl. crane) demonstrated
Components industrialized after intensive R&D at CERN
Systems in advanced phase of series production
Installation in the LHC underground is planned to start 2028
Summary

## Slide 17
Thank you for your attention !