## Slide 1: HL-LHC WP9 Cryogenics Safety studies
V. Gahier
06 Feb 2025

## Slide 2: Content
Introduction
Preliminary Layout for the protecting devices
Case A : helium circuit overpressure – inventory and preliminary flows
Case B : Helium pipe breach to Insulation vacuum– inventory and preliminary flows
Case C. MCI or any case due to powering energy - inventory and preliminary flows
Way forward

## Slide 3: HL-LHC P1/P5 Cryogenic architecture
QSRG : 4.5K refrigerator providing supercritical helium at 3 bara and 4.6 K
QURCG : Cold compressor box providing cooling capacity at 1.8 K
Users at tunnel level
QPLG : Vertical transfer line (~100 m height)
QXL : Distribution line distributing C,E and returning B,D,F
70 m for the common branch
270 m for the long branch
60 m for the short branch
RM/JM : Return module and junction module at extremities for transient handling and back-up
QSCG : Compressor station providing gaseous helium 20 B

## Slide 4: Operating modes and dependency with adjacent sector
All operating modes (similar as for LHC) will be possible:
    Pressure tests,
    Lock-out,
    Cool-down or warm-up,
    Stable operation at 80K, 20K, 4.5K, 3K, 1.9K, IT@20K-LSS/ARC@nominal,
    Maintenance / Technical stop,
    Intervention at magnets level.
"Only" one refrigerator at P1/P5 does not allow to operate the 2 LSS in a different mode  HL-LHC LSS independent from LHC operation thanks to sectorization.
  HiLumi magnets/users can be cooled by :
    New HL Refrigerators  nominal HL performances
    Adjacent sectors – up to twice the LHC nominal luminosity  Degraded operation
  Flexibility during the maintenance period of the HL-LHC cryoplant thanks to the Junction Module functionalities.
  Possible to cooldown one LSS per point independently.

## Slide 5: Protecting devices releasing helium to environment- Preliminary Layout
PF
RP
RP
RP
PF
SV
RP
PF
RP
RP
SV
RP
RP
RP
RP
RP : relief plate on the insulation vacuum
SV/BD : safety device releasing from helium envelope to environment
PF/VB: fixed point / vacuum barrier
Position of safety devices is preliminary and approximate.
Magnet DCM RP TBC
Foreseen : SV DN100 for QXL / SV DN 200 for the IT.
QXL tunnel design is still in preliminary phase.
PF (TBC)
PF
RP
RP
PF
RP
RP
PF
VB
SV/BD
DFX
SV/BD
DFM
SV/BD
CC
SV/BD
CC
RP
Q1
RP
Q2a
RP
Q2b
RP
Q3
RP
CP
RP
D1
RP
RP
DCM
RP
RP
RP
RP
D2
SV
JM
RM
RP
Unsprang relief valve

## Slide 6: Failure modes and cases considered for helium release in the tunnel
Electrical arc
Static loads
(with adequate margin)
Gas blow by (from HP circuit to LP circuit)
Tube rupture
(full or partial)
Loss of insulation vacuum by air ingress
Loss of insulation vacuum by helium ingress
POWERING
Blocked outlet
Vibration / unplanned mechanical displacement
Tube rupture
(full or partial)
Loss of insulation vacuum by helium ingress
CD
Case A : release via BD/SV due to overpressure in helium envelope
Case C: release via RP due powering. Impact may change according the powering level
Case B: release via RP due pipe breach in vacuum

## Slide 7: Different accesses cases with potential helium release to tunnel environment
Case | A | B | B | C | C
Volume to be protected | Helium | Insulation vacuum | Insulation vacuum | Insulation vacuum | Insulation vacuum
Operating cases | Nominal conditions | First Cooldown | Other Cooldown / Nominal conditions | Powering > 1.1 kA (powering level TBC) | Powering < 1.1 kA (powering level TBC)
Access | Access | NO ACCESS | Access | NO ACCESS | Access
Failure modes | LIV 2 x Static HL | Any line full rupture | Line partial rupture | Electrical arc leading to line full rupture + Quench | Limited electrical arc (partial rupture)
System | DFX DFM CCs RM QXL JM QXL | QXL line C IT CM interco D2 CC DFM DFX | All | IT line M or N D2 DFX DFM CC? | IT D2 DFX DFM CC?
Goal | Sizing of the protecting device | Sizing of the protecting device | Define the release location and stagging | Sizing of the protecting device | Define the release location and stagging

## Slide 8: CASE A - helium circuit overpressure – Preliminary flow and inventory
 | Liquid inventory [kg] | SV design case | SV SP [barg] | SV flow [g/s] | BD design case | BD SP [barg] | BD flow [g/s] | Reference
DFX | ~60 | 2x Static load | 1.8 | 10 g/s | LIV | 2.2 | 550 g/s | EDMS 2365987
DFM | ~50 | 2x Static load | 1.8 | 10 g/s | LIV | 2.2 | 500 g/s | Private communication
CC | ~20 | 2.5 x Static load | 0.75 | 5 g/s | Beam vacuum loss | 1.1 | 3510 g/s | EDMS 1900654
JM line C QXL | <0.05 | LIV | 20 | <10 g/s | NA | NA | NA | TBA
RM QXL | ~15 (TBC) | LIV | 4 | 270 g/s (TBC) | NA | NA | NA | TBA
It is understood that below 1 kg/s, the release in the tunnel does not lead to a helium jam ( refer to Note 2010-057)
Addition of Relief device for the operational case of RM considered.

## Slide 9: CASE B – Helium pipe breach to Insulation vacuum– Preliminary flow and inventory
 | Liquid inventory [kg] | flow [kg/s]
QXL line C (long branch) | 243 | 2.2 - 4.6
IT cold mass interconnect | 418 | TBC
DFX | ~60 | TBC
DFM | ~50 | TBC
CC | ~20 | TBC
D2 | ~70 | TBC
Pressure [bara] | Temperature [K] | Area [mm2] | Diameter [mm]
4 | 4.8 | 124 | 12.6
20 | 65 | 255 | 18
1.3 | 1.9 | 336 | 20.7
1.8 | 10 | 1078 | 37.1
1.8 | 4.55 | 280 | 18.9
15 | 25 | 206 | 16.2
1st cooldown : NO ACCESS
Full tube rupture
Other : ACCESS
Partial tube rupture – 1 kg/s
Local pressure in the vacuum enclosure still be checked with the longitudinal vacuum impedance
It is understood that below 1 kg/s, the release in the tunnel does not lead to a helium jam ( refer to Note 2010-057)
Dynamic simulation to be run for evaluation
Similar to LHC
Above 280 mm2 defined in Access and powering LHC doc
Above 500 mm2

## Slide 10: CASE C – MCI or any other case due to powering energy- – Preliminary flow and inventory
 | Liquid inventory [kg] | flow [kg/s]
IT line M or N | 418 | ~10 (TBC)
DFX | ~60 | 2.4
DFM | ~50 | 0.3
D2 | ~70 | TBC
CC? | ~20 | TBC
 | Liquid inventory [kg] | Diameter of hole [mm]
IT line M or N | 418 | 20.7
DFX | ~60 | 18.9
DFM | ~50 | 18.9
D2 | ~70 | 20.7
CC? | ~20 | TBC
Powering >1.1 kA - NO ACCESS
Full tube rupture + Quench
Powering <x kA - ACCESS
Partial tube rupture – 1 kg/s
Local pressure in the vacuum enclosure still be checked with the longitudinal vacuum impedance
It is understood that below 1 kg/s, the release in the tunnel does not lead to a helium jam ( refer to Note 2010-057)
Work in progress

## Slide 11: Way forward
Sizing to be completed
Impedance in the vacuum enveloppe to be calculated when design is further progressed for the QXL.

## Slide 12: Vacuum safety valves

## Slide 13: Volumes to be protected and protecting devices
QXL
M. Sisti
Vacuum
Helium
D2 – WP3
D. Ramos - A. Lees
IT/D1/DCM – WP3
D. Ramos - R. Van Der Weelderen and P. Tavares
Cold Pow – WP6a
Y. Leclercq –V. Gahier
Crab Cavities – WP4
T. Capelli / L. Dassa - L. Delprat / K. Brodzinski
SYSTEMS
VOLUME TO BE PROTECTED
Beam
Insulation
Beam screen
Thermal shield
Cold mass
Magnet HX
Liquid helium
PROTECTING DEVICES
Safety valve
Burst Disc
Generally for MCI
Requires intervention for replacement
Generally for operating cases
Closes after event
SV spring loaded
Relief plate with spring
Relief plate w/o spring
opens at 69 mbar to 134 mbar
DN65 to DN90
4.5-20 K
~1.5 bar
60-80 K
~18 bar
60-80 K
~18 bar
1.9 K
~1.3 bar
1.8 K
~0.018 bar
or
4.6 K
~1.5 bar
opens ranging 30-165 mbar
DN65 to DN230
opens lower than 10 mbar
DN65 to DN230
Covered by VSC
Case A
Case B, C

## Slide 14: Failure modes – MCI or any other case due to powering energy- CASE C
Electrical arc
Tube rupture
(full or partial)
Loss of insulation vacuum by helium ingress
POWERING
Quench
According to the lesson learnt of 19th of Sept. 2008 incident, the MCI should consider full rupture of the pipe at the magnet interconnection.
Quench and electrical arc failure modes are linked with powering and consequences are linked with the powering level.
One failure mode can provoke other failure modes in cascade (refer to 19th of Sept. 2008 LHC incident)

## Slide 15: Inner triplet process data and inventory (1/2)
Line | ID [mm] | Area** [cm2] | P [bara] | T [K]
N1 / N2 | 50 | 19.6 | 1.3 – 17* | 1.9 – 22.2*
LD | 40 | 12.6 | 1.3 – 17* | 1.9 – 22.2*
Cold mass interco | 100 | 78.5 | 1.3 – 17* | 1.9 – 22.2*
CY1 / CY2 | 14 | 1.5 | 0.05 | 
TS | 34.2 | 9.2 | 10-22 | 60-80
BS | 25.5 |  | 10-22 | 60-80
XB1 / XB2 | 100 | 78.5 | 0.020 | 1.85
*Conditions indicated for a 39.1 MJ quench
** Area indicated is the cross section for corresponding ID

## Slide 16: Inner triplet inventory given in helium litre (2/2)
 |  | DCM | D1 | CP | Q3 | Q2A | Q2B | Q1 | Line N | Total
Length [m] |  | 6.17 | 9.1 | 7.95 | 11.1 | 10.78 | 10.78 | 11.56 | 56 | 
Inventory [kg] | 1.9 K cold mass | 16.3 | 31.0 | 72.4 | 68.0 | 68.0 | 68.0 | 68.0 | 27.6 | 418.2
The total liquid inventory at 1.9 K is much higher (43.5 l/m) than the previous considerations at 25 l/m.

## Slide 17: Configuration in case of access
IP1 ZONE
Many relief plates to be expected:
- Q1 to DFX and QXL "T" below ULx3-x7 cores
- D2/DFM to Q4

## Slide 18: Configuration in case of access
Many relief plates to be expected:
- Q1 to DFX and QXL "T" below ULx3-x7 cores
- D2/DFM to Q4

## Slide 19: Reminder of all LHC failure modes
Extract of Preliminary risk analysis of the LHC cryogenic Project Note 177.

## Slide 20: Failure modes leading to helium circuit overpressure - CASE A
Quench  helium release to line D via quench valve
Static loads
(with adequate margin)
Gas blow by (from HP circuit to LP circuit)
Loss of insulation vacuum (LIV) by air ingress
POWERING
Blocked outlet
Helium is released to the atmosphere when it is not possible to collect it in the line D (low pressure equipment such as CC, Cold powering system, RM module)
When the helium release is limited, as an example: protection of double valves system at JM

## Slide 21: LHC model benchmark
 | Cold mass | Header C | QRL vacuum jacket
Pressure [bar] | 1.3 | 3.6 | 10-9
Temperature [K] | 1.9 | 4.6 | NA
Helium sub-sectorization [m] | 214 | 3300 | NA
Vacuum sub-sectorization [m] | 214 | 428 | 428
Helium Mass per sub-sector [kg] | 475 | 3300 | NA
Volume per sub-sector [m3] | 3.21 | 26 | 88.04
Diameter | 0.58 | 0.1 | 0.61
Area of heat transfer [m2] | 389.93 | 134.46 | 820.2
Two cases were considered as sizing for LHC for helium discharge in the tunnel (prior the sept 2009 incident)
  Jumper connection rupture – air to insulation vacuum – not considered for HL-LHC
  QRL line C rupture to insulation vacuum
Those cases were modelled in Ecosim for benchmark.
Extract from PN 381 – helium discharge and dispersion in the LHC accelerator tunnel in case of cryogenic failure
Max ~ 3kg/s
Max ~ 28kg/s

## Slide 22: QRL line rupture
 | Header C
Heat load [W] | 40200
Heat Load [W/cm2] | 0.03
SV on vacuum [m2] | 3 x 0.005
SV set pressure [bara] | 1.3
Vacuum initial temperature [K] | 75
Orifice diameter [mm] | 100
Max ~ 3kg/s
3 SVs of DN100 were considered.
Heat load as per PN381.
Vacuum initial temperature considered to the shield temperature.
Max helium flow rate discharged to the atmosphere is similar to the value found in PN381 though the opening occurs after ~20 s whereas it occurs after 2 min 40 in PN381.

## Slide 23: HL-LHC model – case B
 | Cold mass IT | Header C Long branch | QXL vacuum jacket
Pressure [bar] | 1.3 | 4 | 10-9
Temperature [K] | 1.9 | 4.8 | NA
Helium sub-sectorization [m] | 60 | 530 | NA
Vacuum sub-sectorization [m] | 60 | 155 | 155
Helium Mass per sub-sector [kg] | 418 | 275 | NA
Volume per sub-sector [m3] |  | 2.3 | 30.7
Diameter | 0.58 | 0.065 | 0.6
Area of heat transfer [m2] | 113 | 1.13 – 17.55 | 292
Cases considered :
  1. Line C for QXL – vacuum sectorization limited between fixed point
    Partial – 189 mm2
    Full
  2. Cold Mass IT
    Partial
    Full at interconnect
For helium leak to insulation vacuum, the heat load considered is the convective transfer from the vacuum space at the shield temperature to the cold mass.
Heat coefficient is considered to 17 W/m2/K.
Heat load is calculated to ~ 0.15 W/cm2 versus 0.03 W/cm2.

## Slide 24: QXL line C full rupture – case 1
 | Header C 0.03 W/cm2 | Header C 0.15 W/cm2
Heat load [W] | 46500 | 232500
Heat Load [W/cm2] | 0.03 | 0.15
SV on vacuum [m2] | 0.02 | 0.02
SV set pressure [bara] | 1.3 | 1.3
Vacuum initial temperature [K] | 90 | 90
Orifice diameter [mm] | 65 | 65
Peak flow [kg/s] | 2.2 | 4.6
3 SVs of DN100 (assumed at 5000 mm2 each) were considered.
Vacuum initial temperature considered to the shield temperature at 90 K
Peak flow in the vacuum is 4.6 kg/s.
Heat load : 232500 W
Heat load : 46500 W

## Slide 25: QXL line C partial rupture – case 1
 | Header C 0.03 W/cm2 | Header C 0.15 W/cm2
Heat load [W] | 46500 | 232500
Heat Load [W/cm2] | 0.03 | 0.15
SV on vacuum [m2] | 0.02 | 0.02
SV set pressure [bara] | 1.3 | 1.3
Vacuum initial temperature [K] | 90 | 90
Orifice diameter [mm] | 12.6 | 12.6
Peak flow [kg/s] | 0.5 | 0.7
3 SVs of DN100 (assumed at 5000 mm2 each) were considered.
Vacuum initial temperature considered to the shield temperature at 90 K
Peak flow in the vacuum is 4.6 kg/s.
Heat load : 232500 W
Heat load : 46500 W

## Slide 26: Pressure drop evolution versus the discharge length
Hypotheses:
  DN200 SV: kv = 900 m3/h
  Vacuum enclosure: free section = 0.35 m2, hydraulic diameter = 135 mm
  Mass flow = 1 kg/s