## Slide 1: Detector Cooling
8th Workshop on LHCb Upgrade II
Wiktor Byczynski

## Slide 2
VELO
  Pixel~ 4 kW (temp betwen -40°C to – 100°C)
    CO2 2PACL
    Krypton
    Cryogenics
    Other (not 1 phase)
RICH I + RICH II
  SiPM ~10 kW ~ -190 °C
    Cryogenics
  Electronic Readout ~ 20 kW
    Demi Water
UP
  Pixel 20 kW (temp betwen -20°C to – 40°C)
    CO2 2PACL
  Electronic Readout
    Demi Water
Magnet Stations
  Electronics Readout 3 – 8 kW +15°C
    Mixed Water/Demi Water
  SiPM ?? kW temp betwen ?? °C (sensor)
    CO2 2PACL
    Mixed Water/Demi Water/Chilled Water
    Other (1 phase)
SCiFi/MT
  SiPM ~ 3 kW ~ -190 °C
    Cryogenics
  Front End
    Demi Water
  Pixel ~54 kW
    CO2 2PACL
    Other
  Pixel Patch Panel Cooling ?? kW, ?? °C
    Other (1 phase?)
TORCH
  MCP 4.15 kW temp between 10°C to 15°C
    Mixed Water
    Other
  SiPMs ?
    Cryogenics
MUON
    Mixed Water
Cooling Requirements
* differences compared to :
7th Workshop on LHCb Upgrade II

## Slide 3
Cooling Requirements
UII Cooling Technologies
CO2
Water
Others
Cryogenics

## Slide 4
Cooling Requirements
UII Cooling Technologies
CO2
Water
Others
Cryogenics

## Slide 5
K.Sliwa
Y.Herpin
2PACL CO2 – ATLAS & CMS Upgrade example

## Slide 6
3 head unit
90kW CO2 @ -40°C
2 head unit
60kW CO2 @ -40°C
1 head unit
30kW CO2 @ -40°C
How many units ?
1 unit per detector
no coolant sharing
process parameters flexibility
Redundancy/backup mode?
Sharable units
coolant sharing
process parameters must be the same
  DP setting
  Temperature setpoint
Redundancy/backup mode?
Sharable unit + Back Pressure Regulator
require testing the principle
coolant sharing
process parameters flexible
Redundancy/backup mode?

## Slide 7
CO2 Supply lines ( Accumulator, main plant, detectors)
CO2 Primary circuit (Main plant, Main chiller on surface)
3 x 440 l (for example)
~ 50 m (straight line)
~ 20 m (straight line)
+ 100 m to the surface
2PACL CO2 system piping – Upgrade II
Pipework in LS3 ?
5th MT workshop link

## Slide 8
New cooling services building ?
O.Jamet
CMS – primary chiller CO2
Pipework in LS3 ? +Subcooler on surface ?

## Slide 9
Long Term Schedule
Communicate
needs - baseline
Timeline - prediction
Potential “window”
for EP-DT development
Groups availability
should increase
Latest start date
of production process
CO2 2PACL & CO2 chiller

## Slide 10
Cooling Requirements
UII Cooling Technologies
CO2
Water
Others
Cryogenics

## Slide 11: Cryogenics
2828/U0-404
Surface
O.Jamet
2828/W2-001
SciFi Manifold
Use for testing ?
2829/U0-A01
J.Liberadzka-Porret

## Slide 12
PX84 UGC1 (2831)- ?

## Slide 13
PX84 UGC1 (2831) – Will it fit?
Yes!
Opening enlargement required; structural calculations necessary.
O.Jamet

## Slide 14
Phase Separator
Pumps
Subcooler
Regulation Valve Boxes
Cryogenic system piping – Upgrade II
Vent line (to the surface)
Backup Supply line (to the surface dewar)
Primary circuit (phase separator – subcooler)
Supply line (Nitrogen to the detectors)
5th MT workshop link
Pipework in LS3 ?
Preliminary – may not be possible

## Slide 15
Phase Separator
Pumps
Subcooler – on surface ?
Regulation Valve Boxes
Cryogenic system piping – Upgrade II
Vent line (to the surface)
Backup Supply line (to the surface dewar)
Primary circuit (phase separator – subcooler) 2 options
Supply line (Nitrogen to the detectors)
5th MT workshop link

## Slide 16
Subcooler on surface?
O.Jamet
?
Feasible to install on surface with additional
hardware (pumps, vessel, etc.) - possibly close to the shaft
Determine safety implications of long vertical transfer
lines with permanent presence of liquid nitrogen.

## Slide 17
Timeline - prediction
System commissioning
Surface subcooler
commissioning (if all installed)
Vertical transfer line
Safety approval
Requirements freezing
deadline
Long Term Schedule

## Slide 18
Cooling Requirements
UII Cooling Technologies
CO2
Water
Others
Cryogenics

## Slide 19
Cooling Requirements
UII Cooling Technologies
CO2
Water
Others
Cryogenics
Interest in Krypton project?
Interest in different technology?
  * Not considering to use NOVEC after LS4

## Slide 20
Summary
Check requirements – communicate changes
To anticipate potential pipework in LS3 – clear view of system structure and its capacity is necessary
Cryogenics project – approval of long active vertical transfer lines in shafts are necessary
Provide feedback on interest in other cooling technologies (for example Krypton)

## Slide 21: Thank You!