## Slide 1: A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Vito Vizziello
21/01/2025
TE-MPE-EP

## Slide 2: What is the UQDS and PDSU patch panel
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
For the upgrade of the LHC to HL-LHC, the patch panel represents an element of the Quench Detection System that accomplishes the complex aim of mapping multiple signal sources to multiple destinations.
Vito Vizziello TE-MPE-EP

## Slide 3: Importance of Patch Panel during Hi-Lumi
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Patch Panel
ELQA measurements can be done, at any moment, directly from the Patch Panel if radiation level around IFS boxes placed on the magnet cold mass are high.
ELQA measurements can be provided without the need to disconnect the quench detection system.
Conveying all the needed signals from several IFS boxes directly to each specific UQDS.
Possibility to use a standard hardware configuration for UQDS with fewer risks to make mistakes with the cabling.
Optimizing the time and make it easy during the local interventions.
Vito Vizziello TE-MPE-EP

## Slide 4: General architecture of the Patch Panel
The Patch Panel collects INPUT signals from:
IFS boxes of the magnets
The current sensor boxes
Another patch panel from a different rack.
Internally the patch panel is routed for driving each single INPUT signal to a specific OUTPUT.
The Patch Panel dispatches OUTPUT signals to:
UQDS  according to the configuration needed for each protection unit.
ELQA  reproducing on a dedicated area the same pin-out/connector configuration as for the IFS boxes for each magnet.
Another patch panel from a different rack.
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Vito Vizziello TE-MPE-EP

## Slide 5: View of the Patch Panel
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Front side: ELQA measurements
Back side: Input / Output
current sensors / other racks
All the Patch Panels are different between each other; every rack has its own patch panel.
Vito Vizziello TE-MPE-EP

## Slide 6: IT-STRING Patch Panel
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Universal Quench Detection System
Protection Device Supervision Unit
Vito Vizziello TE-MPE-EP

## Slide 7: Development of the Patch Panel
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
All PCB based (no wires).
PCB is housed in a sandwich: Metal plate, spacer, PCB, spacer, Metal plate.
Connector housings are mounted on the metal plate, both sides, and are connected directly to the PCB via the pin-matrix.
Vito Vizziello TE-MPE-EP

## Slide 8: Development of the PCB
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
PCB size: 3U, 6U, 9U
Number of layers of the PCB: 8
Number of dielectric layers: 13
Vito Vizziello TE-MPE-EP

## Slide 9: HV test validation
A switchboard for valuable signals, the UQDS and PDSU patch panels ...
Vito Vizziello TE-MPE-EP
HV test validation by TE-MPE-PE
The QDS Input Patch Panel must withstand a minimum of 2.5 kV for 60 s with no breakdown and a maximum leakage current of 10 µA.
Each connector at 1 kV must have a leakage current of less than 0.1 µA after 60 s.

## Slide 10
Thank you