## Slide 1: Observations of high frequency noise in turn-by-turn spectra of LHC beams
BE-ABP, SY-EPC, EN-EL and many more..
234th WP2, 13/02/2025

## Slide 2: Overview
Observations from the LHC:
  Power supply ripple in transverse beam spectrum
  Source of emittance growth with unknown origin both at injection and top energy
Tests with main dipole power supply active filters
Impact of transverse damper
Measurements of UPS noise & tests with beam
Impact on beam performance

## Slide 3: LHC observations: Power supply ripple
50 Hz harmonics
50 Hz harmonics
50Hz power supply ripple systematically observed in the transverse LHC spectrum in both beams and planes (mainly in H-plane).
Several studies confirm that it is a real beam excitation in the form of dipolar perturbations.
Very high frequencies also present (~8 kHz while ~11 kHz LHC revolution frequency)
Spectrum from bunch-by-bunch and turn-by turn position measurements
“High frequency cluster”
“Low frequency cluster”

## Slide 4: LHC observations: Power supply ripple
Low-frequency cluster & High-frequency cluster:
Multiple 50 Hz harmonics.
Similar frequency modulation from the mains, with f-modulation amplitude proportional to the order of harmonic.
“High frequency cluster”
“Low frequency cluster”
50 Hz in the beam, normalized
50 Hz mains

## Slide 5: LHC observations: Power supply ripple
Origin of high-frequency 8 kHz cluster is not understood:
  Clear amplitude increase at the end of the ramp when reaching 6.8 TeV.
  Sensitivity to tune trims consistent with dipolar excitations.
  Significantly attenuated amplitude during p-p ref Run (2.68 TeV).
  Impact on performance is unclear, reproducible fill-by-fill.
Nominal fill
p-p ref

## Slide 6: LHC observations: Emittance growth at injection
Emittance growth mechanism at injection not fully understood:

## Slide 7: LHC observations: Emittance growth at injection
Emittance growth mechanism at injection not fully understood:

## Slide 8: LHC observations: Emittance growth at injection
Emittance growth mechanism at injection not fully understood.
o Measured emittance growth for H & V
x IBS model emittance growth for H & V
Emittance growth in H with unknown origin after subtracting IBS contribution
Max. brightness
-20% brightness
-60% brightness
Measurements
IBS + 0.2 μm/h
  Comparison of measured emittance growth & bunch length evolution against theoretical IBS model.
  Horizontal plane:
    Systematically larger in B1H: ~0.6 μm/h in addition to e-cloud:
      0.4 μm/h from IBS.
      0.2 μm/h of unknown origin:
        even with single bunches.
        brightness independent.

## Slide 9: LHC observations: Emittance growth at injection
Emittance growth mechanism at injection not fully understood.
o Measured emittance growth for H & V
x IBS model emittance growth for H & V
Emittance growth in H with unknown origin after subtracting IBS contribution
Max. brightness
-20% brightness
-60% brightness
Measurements
  Comparison of measured emittance growth & bunch length evolution against theoretical IBS model.
  Horizontal plane:
    Systematically larger in B1H: ~0.6 μm/h in addition to e-cloud:
      0.4 μm/h from IBS.
      0.2 μm/h of unknown origin:
        even with single bunches.
        brightness independent.
  Vertical plane:
    ~0.1-0.3 μm/h in addition to e-cloud (B1 & B2).
      Low vertical dispersion & good coupling control  small IBS contribution.
      Measurements suggest some brightness dependence  possibly underestimating IBS or emittance exchange with horizontal in the modeling.
      Linear increase of emittance over time.
IBS + 0.2 μm/h

## Slide 10: LHC observations: Emittance growth at collisions
Emittance growth of unknown origin also during collisions:
  Cannot be fully explained by IBS models.
  Vertical emittance expected to be shrinking due to SR.

## Slide 11: LHC observations: Emittance growth at collisions
Emittance growth of unknown origin also during collisions:
  Cannot be fully explained by IBS models.
  Vertical emittance expected to be shrinking due to SR.
Luminosity model with IBS & SR

## Slide 12: LHC observations: Emittance growth at collisions
Emittance growth of unknown origin also during collisions:
  Cannot be fully explained by IBS models.
  Vertical emittance expected to be shrinking due to SR.
Impact on integrated luminosity:
2-3% loss for fills that reached optimal fill length & τ=2.5 h
Luminosity model with IBS & SR & extra emittance growth

## Slide 13: Tests with main dipole PC active filters
Simple modifications of main dipole power supplies combined with beam measurements: → Experiments with main dipole active filters:
  Responsible for attenuation of 50 Hz ripple.
  Enabling & disabling active filters sector by sectors and observing beam’s response.

## Slide 14: Tests with main dipole PC active filters
Status of active filter per sector
Beam spectrum
h=12
h=12
Clear impact on low-frequency cluster when enabling & disabling active filters.
All eight power supplies contribute to this effect → power supply ripple distributed in the whole ring.
For the same harmonics, different response between Beam 1 & Beam 2→ attributed to their different phase advances.

## Slide 15: Tests with main dipole PC active filters
Amplitude evolution of beam harmonics up to 3.6 kHz (h=72)
h=12
Status of active filter per sector
Clear impact on low-frequency cluster when enabling & disabling active filters.
All eight power supplies contribute to this effect → power supply ripple distributed in the whole ring.
For the same harmonics, different response between Beam 1 & Beam 2→ attributed to their different phase advances.
Beam spectrum

## Slide 16: Impact of transverse damper
B2H
Standard setting
regular-BW cycle
Fill 7033, Stable beams
Special settings
Special cycle ADT extended-BW
Fill 7035 Stable beams
Increasing the transverse damper gain is beneficial: Clear reduction of harmonics’ amplitude
Run 2
Run 3

## Slide 17: Measurements of UPS noise
UPS
B9000 100 kVA UPS BA7
Same type in the LHC
Measurements of UPS output spectrum (same type as the ones in the LHC) to determine if possible candidate for high-f cluster:
  To determine if UPS noise spectrum contains 50 Hz harmonics around 8 kHz as observed on the LHC beam spectrum.
  To determine if spectral components are synchronized to the mains as observed on the LHC beam spectrum.
Changed mode of operation of a few UPSs during dedicated measurements in the LHC with beam.

## Slide 18: Measurements of UPS noise
Link for UPS noise measurements in SM18
UPS noise spectrum
UPS modes of operation
Measurements of spare UPS in SM18 thanks to EN/EL: UPS output voltage spectrum very similar to transverse LHC beam spectrum in terms of ripple→ good candidate to study
Different modes of UPS operation:
Nominal
On battery
Static & manual bypass

## Slide 19: Measurements of UPS noise
Nominal to battery mode
Changing mode of UPS operation → different UPS output voltage spectrum → Can these changes be detected on the beam spectrum as well?
On battery: Clear change of UPS spectrum (loss of synchronization with mains), can be easily detected.
Bypass: Change of UPS spectrum (change of harmonics’ amplitude), not so easy to detect.

## Slide 20: Beam spectrum during SR4 UPS modifications

## Slide 21: Beam spectrum during SR4 UPS modifications
Data from Réseau de Transport d'Électricité

## Slide 22: Beam spectrum during SR4 UPS modifications
No loss of synchronization during tests

## Slide 23: Impact on beam performance
Simulations reproducing the ripple spectrum observed in operation indicate that the high-f cluster has an impact on performance.

## Slide 24: Conclusions
50 Hz dipolar power supply ripple systematically observed in transverse LHC beam spectrum up to high frequencies (~8 kHz).
Origin of harmonics up to 3.6 kHz are the power converters of the main dipoles. Active filters tests demonstrated that frequencies up to 3.6 kHz are passing from the power converter to the beam.
Source of high-frequency harmonics (~8 kHz) remains unknown. Their amplitude significantly increases at the end of the ramp and spectrum is reproducible fill-by-fill. Did not observe any “atypical” behavior that could pinpoint to the source. A lower amplitude was only observed during special runs (2.7 TeV instead of 6.8 TeV)
UPS noise signature matches beam observations: 50 Hz harmonics around 4 kHz & 8 kHz. Dedicated experiments switching some UPS in SR4 to “battery” mode affected only a few low-order harmonics (550, 750, 1150, 1950, 2050, 3150 Hz) only on B1, no impact (loss of synchronization to the mains) on high-f cluster. Testing all UPSs at top energy cannot be done without remote control for UPSs that require access. Switching to battery mode is the clearest signature to detect in the beam spectrum.
Increasing the transverse damper gain reduces amplitude of harmonics.
There is an unknown source of emittance growth at injection (brightness-independent) and during collisions, which cannot be explained by current models. It remains unclear whether this is related to power supply ripple.

## Slide 25: Backup

## Slide 26: LHC observations: Power supply ripple

## Slide 27: LHC observations: Power supply ripple

## Slide 28: Observations in Run 3
B1H
B2H
B1V
B2V
Steps for calibration:
https://codimd.web.cern.ch/s/V1pL7RIBp
Calibrated spectrum for fill 8496, 2390 bunches, Stable beams: similar to what was considered for Run 2.

## Slide 29: Introduction
Harmonics of mains power frequency (50 Hz):
  Observed in several unrelated instruments.
  Visible in all beam modes, fills, planes & both beams.
  Not present without beam (noise of instruments).
  Dipolar excitations, not sidebands around betatron tune.
  Similar observations of high-order harmonics in the form of dipolar excitations in other accelerators (Tevatron, RHIC).
  Several observations: real beam excitations, not an instrumentation artifact.
Beams dumped
Betatron tune

## Slide 30: Comparison of Beam 1 & Beam 2 spectra
~10-3 σ
B1
B2
Larger amplitudes of 50 Hz harmonics by factor of two in Beam 1 compared to Beam 2.
Main impact on the horizontal plane → consistent with dipolar field error.
Maximum amplitude of high-frequency cluster ~10-3 σ.
Stable Beams

## Slide 31: UPS modes
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
ACin1
ACin2
Switching frequency (info from Borri)
Inverter: 4 kHz
Rectifier: 7.5 kHz

## Slide 32: UPS modes
ACin1
ACin2
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
On battery: Battery→ Inverter→ Load
In case of power failure.
In our measurements, no synchronization with ACin1 and ACin2.

## Slide 33: UPS modes
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
On battery: Battery→ Inverter→ Load
In case of power failure.
In our measurements, no synchronization with ACin1 and ACin2.
Static bypass: ACin2 → Switch → Load
Switches automatically to maintain power continuity in case of inverter failure.
ACin1
ACin2

## Slide 34: UPS modes
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
On battery: Battery→ Inverter→ Load
In case of power failure.
In our measurements, no synchronization with ACin1 and ACin2.
Static bypass: ACin2 → Switch → Load
Switches automatically to maintain power continuity in case of inverter failure.
Maintenance bypass: Acin2 → Load
Manual action required.
ACin1
ACin2
Notes: c

## Slide 35: Spectra in all UPS modes
Normal mode
On battery
Static bypass
Maintenance bypass
Change of spectrum
Noise from the mains
Noise from the inverter
Notes: c

## Slide 36: Spectrogram in normal mode
Normal mode
Notes: c

## Slide 37: Spectrogram in normal mode
Normal mode
Common jittering from the mains
Notes: c

## Slide 38: Spectrograms in all UPS modes
Normal mode
Static bypass
Without synchronization with ACin1 & 2
On battery
Maintenance bypass
Notes: c

## Slide 39: Spectrograms in all UPS modes
Normal mode
On battery
Static bypass
Maintenance bypass
Notes: c

## Slide 40: MD overview
Second MD:
  At top energy so that the 8 kHz cluster is clearly visible.
  With 3 trains of 48 bunches to have a symmetrical filling scheme.
  UPS in SR4 switched twice to battery mode and back to nominal operation
B1

## Slide 41: MD overview
2 MDs (July & November)
First MD:
  at injection, with 6 pilots and then 4 nominals
  UPS modifications from EN/EL:
    First, EZS1/45X and EZS11/45X (in cascade) in UX45 (access needed) switched from “nominal” configuration to “manual bypass” and then back to “nominal”. Not possible to switch to “battery mode” without remote control.
      UPS connected to (H. Timko): ADT, racks for klystrons, LLRF crates for cavity control and longitudinal diagnostics in UX45.
    Then, EBS11/4R in SR4 (no access needed) switched from “nominal” configuration to “battery”, “static bypass”, “manual bypass” and back to “nominal”.
      UPS connected to (H. Timko): ADT, LHC beam control (RF frequency generation, beam phase loop, synchronisation etc.), longitudinal diagnostics in SR4 (APWL, beam spectra, longitudinal ObsBox)