## Slide 1
LCLS-II Cryogenic Software
ICALEPCS 2025 - PLC Workshop
Andrew Wilson / Staff Engineer / andreww@slac.stanford.edu / Electronics Engineering Division
September 20, 2025

## Slide 2: Overview
LCLS-II control architecture
How did this happen?
How will we fix this?

## Slide 3: LCLS-II Cryogenic System
Scope
60 Cryomodules
2 Cryoplants
22 PLCs
>Tens thousand devices
Software
PLC control
EPICS HMI
16
17
18
19
20
21
22
23
24
25
26
27
28
43
30
31
33
34
35
VB
DB2
FC6
FC7
36
37
38
39
40
41
42
VB
56
47
48
49
50
51
52
53
54
55
EC4
01
EC1
15
04
05
06
07
08
09
10
11
12
13
14
FC5
DB1
FC4
FC3
03
HL01
HL02
02
FC2
FC1
L1
L0
L2
L3
29
44
45
59
57
58
46
DB3
EC
2
L4
IB3

## Slide 4: LCLS-II Cryogenic Control Architecture
CP1 2KCB
CP2 2KCB
DB1 PLC
DB2 PLC .
DB3 PLC
IO Responsibilities
UTILITY

## Slide 5: LCLS-II Cryogenic PLC Code Structure
Main Task Loop
IO Buffering
  IO Cards mapped to tags used internally and monitored by EPICS
  Profibus data parsed and mapped to internal tags
  Produced/Consumed tags mapped to internal tags
  Calculations
  Calculated signals
    Temperature Delta
    Rate of change
    Averages
    Flows
  Mapped to internal PLC tags
  Device Processing
  One routine per device type
  Evaluates information relevant to the device
    Filters
    Interlocks
    Alarms
    Control Loops
    Sequences
    Specific processes defined in functional analysis
    Multiple unique steps
    Not repetitive

## Slide 6: LCLS-II Cryogenic Control Architecture
CP1 2KCB
DB1 PLC
DB2 PLC .
DB3 PLC
Control Responsibilities
CP2 2KCB

## Slide 7: LCLS-II Cryogenic Control Architecture
Issues
CDS and Cryoplant PLCs use different objects
Cryoplant PLCs use standard objects and program execution style
CDS PLC developed separately and uses its own objects and style
Makes it difficult for others to understand the system well enough to support it
Large amounts of integration work at the end of the LCLS-II project
PLC code developed independently as integrated controls was not scoped
Current architecture a result of this last minute un-scoped integration work, instead of thoughtful planning
Centralized control required large amounts of produced/consumed tags – Over 7,000 per PLC
Highlights
All Code is based on clear documentation
Functional Analysis matches code in naming, structure, and flow
Naming conventions defined and followed
Hardware architecture matches the system well
PLCs connect to logical hardware
Interface points between PLCs are clear

## Slide 8: How Did This Happen?
Development
Cryoplant was developed at JLAB
Functional Analysis
Controls Hardware
Controls Software
Distribution System Controls developed at SLAC
PLC and EPICS code developed by controls department
Only basic requirements from cryogenic system provided
SLAC Cryogenic Department Organized
This division to own the cryogenic system
Includes controls engineers
Inherited only project development documentation which did not cover operational procedures, maintenance, or other things not funded by the project
Developed thorough documentation and standards
Future system owner not involved in development!
Integration not scoped because interfaces were defined!

## Slide 9: How Did This Happen?
Integration
Cryoplant developed thorough documentation and rewrote cryoplant software to match
  Allowed them to have clear, maintainable documentation
  Included many requirements that are needed to be able to operate the system practically
  Global controls
  Automated sequences
Project did not fund integration but handed off to operation
  Schedule was already stretched without this work
  We ended up rewriting the distribution code in the last 2 months of the project to match cryoplant functional analysis

## Slide 10: How Will We Fix This?
What is an ideal system?
Well documented
Consistent
Modifiable
Support new operating configurations
How to make it?
Build based on cryogenic group’s documentation
  System owner defined
  Consistent vocabulary
  Clear flow from requirements to descriptions to code to procedures
Define coding standard
  Consistent objects
  Consistent processing
  Consistent naming
Local control
  Local PLC responsible for all functions of connected devices
  Share dozens of needed signals, not all
  One source of truth
  Manageable amount of interfaces allows multiple configurations
One team

## Slide 11: LCLS-II Cryogenic Control Architecture
CP1 2KCB
CP2 2KCB
DB1 PLC
DB2 PLC .
DB3 PLC
IO responsibilities local control responsibilities
UTILITY