## Slide 1: NN-based MPC for energy efficient HVAC systems for CERN accelerators
Nikolina Bunijevac EN/CV/CL
Notes: The Cooling & Ventilation group (CV) is responsible for the design, installation, commissioning, operation and maintenance of the cooling systems, pumping stations, air conditioning plants and fluid distribution systems for the whole of CERN’s accelerator complex, its experimental areas and some of the special cooling systems of the LHC experiments’ sub-detectors as well as for strategic technical installations such as the Computer Centre.

## Slide 2: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 3: NN-based MPC for energy efficient HVAC systems for CERN accelerators
heating, ventilation, air conditioning

## Slide 5: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 6: Research motivation
Chart: CERN/LHC electricity consumption
| Cooling and ventilation | other
LHC electricity consumption | 0.12 | 0.88
  Following global sustainability concerns, “pursuing actions and technologies aiming at energy savings and reuse” is listed as one of the main objectives for 2021-2025 at the European Organization for Nuclear Research (CERN). This objective extends to the Cooling and Ventilation group.

## Slide 7: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 8: Controls optimization

## Slide 9: Controls optimization
Classical feedback Controller
Notes: pid

## Slide 10: Controls optimization
Classical feedback Controller
PID
Notes: pid

## Slide 11: Controls optimization
Classical feedback Controller
Model Predictive Controller
- prediction horizon
external information
PID

## Slide 12: Modelling

## Slide 13: System: Air Handling Unit (HVAC311)

## Slide 14: System: Air Handling Unit (HVAC311)

## Slide 15: System: Air Handling Unit (HVAC311)
Controlled variables

## Slide 16
Physics-informed approach

## Slide 17: Modelling: methodology
Notes: Advantages of data-driven model
Reduced Development Time and Cost
Flexibility
Efficiency (reduced computational load)
Disadvantages
Lack of Insight into Internal Processes
Dependency on Quality of Data
Limited Accuracy in Novel Situations

## Slide 18: Modelling: methodology – black-box
Zone: autoregressive and dynamic
AHU blocks: steady-state

## Slide 19: Modelling: methodology – black-box
AHU blocks: steady-state

## Slide 20: Modelling: methodology – black-box
Zone: dynamic
AHU blocks: steady-state

## Slide 21
Steady state models
Dynamic model
AHU
Zone

## Slide 22
Steady state models
Dynamic model
AHU
Zone

## Slide 23: Example: cooling coil

## Slide 24: Example: cooling coil & zone

## Slide 25: Optimization

## Slide 26: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 27: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 28: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 29: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 30: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 31: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 32: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 33: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes

## Slide 34: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes
Tricks : start with actuators off – even less than 2s solution found
Also limit actuators controls change within function to create individuals
Penalize sudden changes in supply T (expect this to reflect In zone as well)
Start where stopped: for actuators

## Slide 35
4h
Example: MPC solution
4h

## Slide 36
4h
Example: MPC solution

## Slide 37
4h
Example: MPC solution

## Slide 38: Next step
  thorough comparison between classical controls and MPC
  test zone on larger dataset
  If needed, MPC optimization upgrade for faster convergence

## Slide 39: Discussion

## Slide 40: Extra slides

## Slide 41: MPC for HVAC Modelling upgrade: dataset

## Slide 42: Modelling: methodology – black-box
 | AHU (4 NNs) | ZONE (1 NN)
Number of parameters | ~50 (61, 51, 51, 46) | 182
Size of dataset (6:1 training:test) | 2290 | 1565
Individual precision Mean abs error [*C] | ~0.25 (0.39, 0.33, 0.09, 0.17) | 0.17 (0.25, 0.09)

## Slide 43: Modelling: methodology - update
Steady state
Prediction in next point in time
AHU - fast
Zone - slow

## Slide 44
Steady state
Prediction in next point in time
AHU
Zone

## Slide 45
Steady state
Prediction in next point in time
AHU
Zone
Problems with RNN initialization

## Slide 46: MPC for HVAC: Genetic algorithm: implementation
- prediction horizon: 2h (Ts = 15min  8 points)
- optimization variable binary representation for 1 pt in time:
  bits in total: 8*12 = 96 bits/optimization
- parameters:

## Slide 47
- temperatures within limits
- advance controls: damper management
- PID: more active components

## Slide 48: MPC for HVAC Results
- constraints violated
- unusual system response
- unusual PID response

## Slide 49: Conclusion
- promising results, but too optimistic (savings 77% comparing to 20% in literature)
- improvements:
  improving model:
    dataset, architecture, training
  improving optimization algorithm:
    faster execution  faster test comparison
  tunning PID for fair comparison

## Slide 50: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated
Notes: Time for execution: 5minutes