## Slide 1: NN-based MPC for energy efficient HVAC systems for CERN accelerators
Nikolina Bunijevac EN/CV/CL

## Slide 2: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 3: NN-based MPC for energy efficient HVAC systems for CERN accelerators
heating, ventilation, air conditioning

## Slide 5: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 6: Research motivation
Chart: CERN/LHC electricity consumption
| Cooling and ventilation | other
LHC electricity consumption | 0.12 | 0.88
  Following global sustainability concerns, “pursuing actions and technologies aiming at energy savings and reuse” is listed as one of the main objectives for 2021-2025 at the European Organization for Nuclear Research (CERN). This objective extends to the Cooling and Ventilation group.

## Slide 7: NN-based MPC for energy efficient HVAC systems for CERN accelerators

## Slide 8: Controls optimization

## Slide 9: Controls optimization
Classical feedback Controller

## Slide 10: Controls optimization
Classical feedback Controller
PID

## Slide 11: Controls optimization
Classical feedback Controller
Model Predictive Controller
- prediction horizon
external information
PID

## Slide 12: Modelling

## Slide 13: System: Air Handling Unit (HVAC311)

## Slide 14: System: Air Handling Unit (HVAC311)

## Slide 15: System: Air Handling Unit (HVAC311)
Controlled variables

## Slide 16
Physics-informed approach

## Slide 17: Modelling: methodology

## Slide 18: Modelling: methodology – black-box
Zone: autoregressive and dynamic
AHU blocks: steady-state

## Slide 19: Modelling: methodology – black-box
AHU blocks: steady-state

## Slide 20: Modelling: methodology – black-box
Zone: dynamic
AHU blocks: steady-state

## Slide 21
Steady state models
Dynamic model
AHU
Zone

## Slide 22
Steady state models
Dynamic model
AHU
Zone

## Slide 23: Example: cooling coil

## Slide 24: Example: cooling coil & zone

## Slide 25: Optimization

## Slide 26: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 27: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 28: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 29: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 30: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 31: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 32: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 33: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 34: Optimization
optimization function: estimation of electricity consumption for the prediction horizon + penalty
optimization variables:
- constraints:
  control constraints
  variable constraints
genetic algorithm
optimization technique based on evolutionary principles to find solutions to complex problems
(fresh air damper opening),
(cooling coil valve),
(heater command)
binary
embedded in variable coding
penalty when violated

## Slide 35
4h
Example: MPC solution
4h

## Slide 36
4h
Example: MPC solution

## Slide 37
4h
Example: MPC solution

## Slide 38: Next step
  thorough comparison between classical controls and MPC
  test zone on larger dataset
  If needed, MPC optimization upgrade for faster convergence

## Slide 39: Discussion