## Slide 1: EN-HE Updates
HI-ECN3 WP4 - Coordination meeting #10 – C. Duran Gutierrez, R. Rinaldesi – EN-HE
19-03-2024

## Slide 2: Content
ECN3 Transfer tables
  Location of components and Works
Service Building – Equipment installation
  Power room and Control room
  CV Rooms
  Motorized trolley
Ongoing and future assessments
Questions

## Slide 3: ECN3 Transfer tables
2
Location of components and works
Final proposal
Control panel installed outside the shaft
  On the gallery wall, in front of the lift.
Cable reel located outside the shaft, beneath the staircase, behind the lift
  There will be an opening in the wire mesh to allow the cable to pass through, along with a pulley system.
1
2
Possible control panel locations

## Slide 4: ECN3 Transfer tables
Location of components and Works
Small opening
Estimated dimensions = 450 x 70 mm
Exact location to be defined
Pending
Final determination of the control panel’s exact location and cable routing.
Exact location of the opening in the wire mesh for the pulley system.
Final quotation.
ECR
Pulley also located outside the shaft.

## Slide 5: Service Building – Equipment installation
Power Room and Control Room
IMPORTANT
To verify the general dimensions, weights and lifting points of all equipment to be installed.
Restrictions
Available space in the access platforms (3500x2700)
  Front access – 3380 mm width
  Lateral access – 2650 mm width
Height inside the structure – 4300 mm
Door size (2900x1600)
Guardrails (removable)
3380
2650

## Slide 6: Service Building – Equipment installation
Power Room and Control Room
Available equipment for installation
An extension of the access platform will be required to access with a crane
Forklifts (?)
Power room
Control room

## Slide 7: Service Building – Equipment installation
CV Rooms
CV 1
CV G
First draft study analyzing possible sequences for the transportation and handling of CV equipment within the new service building (first installation and maintenance operations)
CV 1 – CV Room on the first floor
CV G – CV Room on the ground floor

## Slide 8: Service Building – Equipment installation
CV Rooms
CV G
CV Room – Ground floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (3) | 2468 x 2484 mm
1
2
3
1
2
3
Option 1 – Transport with trolley through the Cell Operation Room

## Slide 9: Service Building – Equipment installation
CV Rooms
CV G
CV Room – Ground floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (3) | 2468 x 2484 mm
1
2
3
1
2
3
Option 1 – Transport with trolley through the Cell Operation Room
Option 2 – Handling with the crane and final transfer to CV room using a platform/trolley
Crane unloading area

## Slide 10: Service Building – Equipment installation
CV Rooms
CV Room – Ground floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (3) | 2468 x 2484 mm
CV-Room Height | 3600 mm
3600
2484
3000
1500
Precise transport and installation studies for the water tanks must be assessed.
The water tanks must be brought into a horizontal position and then rotated once inside the room.
However  600 mm height margin with the ceiling
ST1A11865_01

## Slide 11: Service Building – Equipment installation
CV Rooms
CV 1
CV Room – First floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (4) | 2468 x 2084 mm
CV-Room Height (beams) | 7350 mm
5500
4000
5100
1
Removable
Guardrail (?)
1
2
4
Option 1 – Transport using a trolley through the Cell Operation Room + lifting with the crane

## Slide 12: Service Building – Equipment installation
CV Rooms
CV 1
CV Room – First floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (4) | 2468 x 2084 mm
CV-Room Height (beams) | 7350 mm
5500
4000
5100
Option 1 – Transport using a trolley through the Cell Operation Room + lifting with the crane
Option 2 – Handling the object from the hall with the crane until it reaches the mezzanine
1
2
Removable
Guardrail (?)
1
2
4

## Slide 13: Service Building – Equipment installation
CV Rooms
CV Room – First floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (3) | 2468 x 2084 mm
CV-Room Height (beams) | 7350 mm
1600
3470
Crane coverage
Based on previous experience, the extra coverage we could gain:
To the wall ≈ + 200 – 300 mm
Long travel ≈ + 1500 – 2500 mm
Height ≈ + 500 mm
Auxiliary
hoist

## Slide 14: Service Building – Equipment installation
CV Rooms
CV Room – First floor | 
Cell operation room Doors 1) and 2) | 2068 x 2084 mm
CV-Room Door (3) | 2468 x 2084 mm
CV-Room Height (beams) | 7350 mm
CV Room – Equipment (first draft) |  | 
AHU unit | 4000 x 1000 x 1000 | 600 kg
Filters | 2314 x 650 x 1746 | 500 kg
Carbon Filter | 3870 x 888 x 1746 | 1110 kg
AHU and Carbon filters simulation handling
Crane coverage
CoG
3300
Proposed solution
Auxiliary hoist (extra crane coverage)
  Capacity to be defined
Example of auxiliary hoist (PR 806)

## Slide 15: Service Building – Equipment installation
Motorized trolley
As discussed in the previous coordination meeting and the 1st BDF-TSAC
Best guiding system to be defined:
Rails  Might pose an issue when sealing the service cell
Therefore, a motorized trolley with multidirectional polyurethane wheels could be the best solution for transferring material from 911 to the service cell.
To be defined
Dimensions and capacity
Power system – Cable reel? Batteries?
  If using a cable reel, how to manage the cabling once the platform is inside the service cell?
  Failure scenarios for each option and potential solutions
Motorized platform with multidirectional wheels (Morello)

## Slide 16: Ongoing and future assessments
Vacuum vessel
Lifting points
Spreader (motorized with auto-locking points)
Door
  Door removal procedure
  Lifting tool
Service cell crane
Specifications and estimated volume
Handling studies (procedures and tooling)

## Slide 17: Questions
CV
Cabling and pipes through the 911 shaft  estimated volume and location within the shaft

## Slide 19: ECN3 Transfer tables
770
2515
9800
3550
2094

## Slide 20: ECN3
SHiP experiment. Cryostat installation
Direct slinging
Dedicated lifting beam
4 lifting points
2 for Tcc8’s hook
2 for ECN3’s hook
2 lifting points for ECN3’s hook
+ bottom support
Similar operations
Studies ongoing
Option 1
Option 2