## Slide 2: Liquid Argon Cryogenics and Cooling Options
T. Koettig
with contributions from: J. Bremer, C. Fabre, J. Rutherford, D. Santandrea, F. Cacherat

## Slide 3: Content
Applications of liquid Argon (LAr) in particle detectors
Introduction to Argon as a cryogenic fluid
Thermodynamics of LAr
Cooling options for LAr
Remarks

## Slide 4: Applications of LAr in Particle Detectors
J. Bremer

## Slide 5: Cryogenics for ATLAS Liquid Argon Calorimeters

## Slide 6
Liquid Argon Cryostats and Cryogenics at CERN
Advantages:
Vacuum insulated cryostat, very low heat input (< 6 W/m2)
Cold vessel can be purged before start of cool-down (very pure liquid needed)
Picture of the ATLAS barrel calorimeter cryostat before lowering into UX15 cavern.
Total liquid argon volume about 50 m3.
Disadvantages:
Quite heavy structure
Large heat load when vacuum is broken
Getting to the limit of what’s reasonable possible for vacuum insulated cryostats

## Slide 7
ATLAS Liquid Argon Calorimeters
Barrel Calorimeter:
  D: 4.3 m; L: 6.5 m
  Weight: 120 t
  Argon volume: 40 m3
Electromagnetic barrel half-wheel
Courtesy of Caroline Fabre

## Slide 8
ATLAS Liquid Argon Calorimeters
Courtesy of Caroline Fabre
End-cap Calorimeter:
  D: 4.3 m; L: 3 m
  Weight: 219 t
  Ar volume: 19 m3
Calorimeters are highly complicated composite structures made of copper, lead, stainless-steel and glass-epoxy… placed in aluminium cryostats

## Slide 9: LAr Neutrino Detectors => Programs at CERN II
2 cryostats in EHN1 => NP02 and NP04
Design, installation and operation of 8x8x8 m3 sensitive volume cryostat and cryogenics system
12.5 m
12.5 m
11.2 m
Total liquid argon volume: 510 m3
Total argon weight: 705 ton
Cryogenics will be supplied via central system, to be designed and installed for this area
Continuous circulation and purification
=> LAr impurity level ≤ 30 ppt (O2 equiv.)

## Slide 10
How could we construct these real large cryostats?
Could we use the membrane technology as already in use for liquefied natural gas storage and ship transport:
Primary membrane: To contain the liquid
Polyurethane foam: to diminish the heat-load ( 1 meter thickness: < 10 W/m)
Secondary membrane: to contain liquid in case of leak primary membrane
Vapour barrier: no condensation of air on cold surface
Support of cryostat on concrete of metallic structure
Example

## Slide 11
Eventual Future LAr Neutrino Detectors
15.6 m
16.0 m
28.6 m
Two cryostats, with about 10 kton liquid argon each
Argon purity < 200 ppt oxygen equivalent (electron life-time > 1.4 ms)
To be installed and operated in a cavern at 1.6 km below ground level
Ready for operation: 2021
LBN at Homestake, South-Dakota
Courtesy: Dune collaboration

## Slide 12: LAr Neutrino Detectors => with CERN Team Contribution
Short Base Line Far Detector
600 ton of liquid Argon
The “upgraded ICARUS” will be installed as Far Detector at Fermilab
Courtesy: Icarus collaboration

## Slide 13: Argon – Cryogenic Properties
T. Koettig

## Slide 14: Cryogenic Fluids
THERMOPHYSICAL PROPERTIES

## Slide 15: Argon as a Cryogenic Fluid
From: Haefer, Kryovakuumtechnik
TTrP=83.8 K
Tc=150.7 K

## Slide 16: Argon as a Cryogenic Fluid
Data source: Refprop, NIST

## Slide 17: Argon as a Cryogenic Fluid
Data source: Refprop, NIST

## Slide 18: Argon as a Cryogenic Fluid
Data source: Refprop, NIST

## Slide 19: Argon as a Cryogenic Fluid
Data source: Refprop, NIST

## Slide 20: Argon as a Cryogenic Fluid
Dynamic Viscosity of Liquid Argon and Nitrogen
Data source: Refprop, NIST

## Slide 21: LAr vs. LN2 natural convection heat transfer
Free convection heat transfer at horizontal cylinder
Nusselt number
Rayleigh number
Parameters:
ε vol. expansion coeff.
ν kinematic viscosity
a therm. diffisivity
l => dTube,outer=10 mm
ΔTtransfer =0.2 K
Data source: Refprop, NIST

## Slide 22: Liquid Argon - Cooling Options

## Slide 23: Argon as a Cryogenic Fluid
87.3 K
94.4 K
Tripel point
p=0.689 bar
T=83.81 K
Data source: Refprop, NIST

## Slide 24: Reliquefection of Evaporated Liquid – Small scale
Cold tip temperature in K
Cooling power in W
Single stage Pulse Rube Refrigerator (PTR)
Liquefaction rate
for nitrogen 1 l/h
Regenerator with internal pulse tube (coaxial design)
300 K vacuum flange
Cold tip

## Slide 25
ATLAS Liquid Argon Calorimeters – Large scale cooling
Courtesy of Caroline Fabre
2.1 bar
End-cap
LAr Tanks
LN2
tank
LN2 pump
Expansion vessel 1.25 bar
5.3 bar
Barrel
End-Caps
LN2 phase separator
Nitrogen
Argon

## Slide 26
ATLAS Liquid Argon Calorimeters - Cooling
Outlet valve controls the system pressure
Inlet valve controls
mass flow
Why control loop like that?
- Pressure release in emergency
Heat loads
- Cooldown: having the possibility to keep the system at the required T(p) level
p
h
PT
001
Enter two-phase area by expansion

## Slide 27
89.3 K
2.5 K
6 K
Cooling options for liquid Argon
Tripel point
p=0.689 bar
T=83.81 K
2.1 bar
2.8 bar
1.25 bar

## Slide 28: ATLAS – FCAL heat transfer study
Pressurized liquid Argon
in the ATLAS - FCAL
p=2 bara, T=87.3 K
Courtesy of Caroline Fabre
1.25 bar

## Slide 29: ATLAS FCAL Heat load generation
Hottest spot at EM shower
Heat flows outwards to HEC, crossing a 12 mm clearance gap between FCal and HEC
LAr is an excellent thermal insulator
Courtesy of John Rutherford

## Slide 30: ATLAS FCAL LAr Gap Convection
FCal
HEC
Heat flows radially outwards
Clearance gap 6 to 12 mm
The 12 mm clearance gap is the biggest obstacle to radial heat flow from the FCAL to the HEC.
Convection improves the transport of heat across the 12 mm clearance gap.
Courtesy of John Rutherford

## Slide 31: FCAL Mock-up => Principle of Operation
Drive heat across a layer of known thermal conductivity
Measure temperature drop
The same amount of heat must cross the liquid argon layer
Measure temperature difference across this layer
Courtesy of Prof. John Rutherford

## Slide 32: ATLAS FCAL Mock-up in the Cryolab
Sample from Univ. of Arizona and components from TU Dresden
Test of the thermal performance of a FCAL mock-up in subcooled LAr bath
Constant LAr level
in the cryostat
Vapor pressure
regulation
Subcooling
Loops using
pressur. LN2
Rotatable
sample support
to simulate all FCAL orientations
α

## Slide 33: ATLAS FCAL Mock-up in the Cryolab
ΔT ≤ 6 K
Subcooled LAr bath
Uniform
subcooling
Setting the
saturation
pressure
Depending on the heat input by the cryostat one needs to cool or heat there.

## Slide 34: ATLAS FCAL Measurement Results
12 mm LAr gap size in the sample, total heat load 25 W => Q= 22 W equivalent , expected for LHC Run 2
T=86.5 K
Vertical position
Horizontal position

## Slide 35: ATLAS Forward Calorimeter Heat Transfer Study
In case of a
12 mm LAr gap
In case of a
6 mm LAr gap
Ratio 0.423
Ratio 0.402
Total
thermal heat transport capability
is almost independent of
gap size in vertical
and horizontal orientation

## Slide 36: Full Large scale LAr cooling for a TPC

## Slide 37: Large scale LAr TPC – Vortex in LAr???

## Slide 38: Conclusion
Argon as a cryogenic fluid gets more and more used for particle physics
Large LAr volume => necessity of non-vacuum insulated vessels operating at atmospheric pressure
Cooling source needs to guarantee LAr saturation pressure of -5 mbarg <pLAr< 20 mbarg
Pressure safety equipment with low set points in respect to ambient
Cooling of LAr by using LN2 => requires relative high pressures pLN2>2.8 bara (pLN2>2.1 bara => TP of Argon) => CERN approach
ODH problematic in pits, underground etc.

## Slide 40: LAr Neutrino Detectors - LN2 Cooled Thermal Shield
Icarus upgrade
Cryolab R&D
=> cooling performance of
thermal shield panels
=> LN2 cooling infrastructure +
two-phase flow distribution

## Slide 41: LAr Neutrino Detectors - LN2 Cooled Thermal Shield
Lateral collector cooling loop: half view
D
C
B
A
AB: bottom collector CD: top collector Cryostat width 20 m
Length of the panels 472 mm
Number of panels = 42
Mass flow total = 84 g/s
Pressure inlet 3.5 bar Temperature inlet 84 K
Goal:
Expansion at each lateral loop inlet -> after JT exp. 87 K, 2.76 bar, 10% quality

## Slide 42: LAr Neutrino Detectors - LN2 Cooled Thermal Shield
Required cooling power and mass flow rates
Mass flow in one lateral loop = 2.0 g/s
Mass flow in one vertical loop = 0.7 g/s ( end caps )
Total Mass flow lateral cooling = 2.0 g/s x 42 x 2 = 168 g/s Total Mass flow vertical cooling = 0.7 g/s x 8 x 2 = 11.2 g/s
Total mass flow = 179.2 g/s = 0.179 kg/s = 644 kg/h/cryostat
Heat flux = 20 W/m2 Heat Load per meter panel = 9.4 W/m
Total Cooling power = 10.2 kW/cryostat
LN2 two-phase flow, vapor quality 10% < x < 40 %