## Slide 2: Refrigeration Cycles and Respective Diagrams
T. Koettig on behalf of the CERN Cryolab

## Slide 3: Content
Cryogenic fluids
Phase diagrams in 3D
Projected diagrams in 2D
T-s vs. log(p)-h diagram
Thermodynamic cycles as application Isentropic, Isenthalpic, HEX
Refrigeration cycles

## Slide 4: Cryogenic fluids

## Slide 5: Cryogenic Fluids
THERMOPHYSICAL PROPERTIES
Fluid | 3He | 4He | N2 | Ar | H2 | O2 | Kr | Ne | Xe | Air
Boiling temperature 1.013 bar (K) | 3.19 | 4.2 | 77.3 | 87.3 | 20.3 | 90.2 | 119.8 | 27.1 | 165.1 | 78.8
Latent heat (evaporation at Tb) kJ/kg | ~7 15.87 @ 1.65 K | 20.91 | 199.1 | 163.2 | 448 | 213.1 | 107.7 | 87.2 | 95.6 | 205.2
Pressure to solidify bara or Ttr in K | 34.4 | 25.4 | 63.15 | 83.81 | 13.8 | 54.36 | 114.9 | 24.56 | 161.4 | -
Density of liquid (at Tb) – kg/m3 | 58.9 | 124.8 | 804 | 1400 | 71 | 1140 | 2413 | 1204 | 2942 | 874

## Slide 6: p-T diagram - Overview of vapor pressures
Liquid
Vapor
From: Haefer, Kryovakuumtechnik

## Slide 7: Latent Heat of Evaporation 3He and 4He
Source: Ventura, The Art of Cryogenics, Fig. 2.5

## Slide 8: p - v - T diagram

## Slide 9
Phase diagrams
The Ideal Gas law
You don’t need
to answer….
Adapted from: Labuhn, Keine Panik vor Thermodynamik, 2011.
T1=294 K
p1=1 bar
p2=3 bar

## Slide 10
p-T diagrams
Nitrogen
https://www.researchgate.net/figure/The-temperature-pressure-phase-diagram-for-nitrogen_fig1_315888614
Source: http://ltl.tkk.fi/research/theory/helium.html
Phase diagrams for N2, 4He and 3He
Helium isotopes show no triple point
Superfluid phases at low temperature
3He first binds two atoms weakly to have a bosonic character => ~ 2 mK
4He
3He

## Slide 11
Critical point transition => opalescence e.g. SF6
Source: https://expvorl.physik.uni-muenchen.de/versuche_waermelehre/ideale_und_reale_gase/kritische_opaleszenz/index.html
Heating a cell with two-phase SF6 from 45 °C => rising p and T => supercritical fluid
Example LHC beam screen heating with 3 bar 4.6 K to 20 K
Start in subcooled (pressurized liquid) to vapor
Still large density change even without classical evaporation
Different diagrams like T-s or p-h are more suited to demonstrate the process
From: Gerhold, Properties of cryogenic insulants, Cryogenics Vol. 38, pp. 1063

## Slide 12
Helium p-T diagrams - effects
4He phase diagram
subcooling in a saturated bath
From: Van Sciver, Helium Cryogenics.
3He phase diagram
Pomeranchuk cooling
From: Enss, Low-Temperature Physics.

## Slide 13: Thermodynamic cycles

## Slide 14
In the restaurant
From: Labuhn, Keine Panik vor Thermodynamik, 2011.
with entropy?

## Slide 15
Thermodynamics of cryogenic refrigeration
First principle [Joule]
Second principle [Clausius]
(= for reversible process)
Hence,
which can be written in different ways:
Carnot factor
introducing entropy S as
From: P. Lebrun, CAS

## Slide 16
300
10
5
2
Thermodynamics of cryogenic refrigeration
He II 1.8 K - ec=166
He 4.5 K - ec=65.7
H2 20 K - ec=14
N2 77 K ec=2.9
Graph for Twarm = 300 K
Carnot effectiveness:

## Slide 17
Our first T-s diagrams
From: Labuhn, Keine Panik vor Thermodynamik, 2011.
e
Here, the state of order is preserved
Isentropic
(Entropy is constant!)
Frictionless, but not adiabatic
Adiabatic, but not
frictionless
e
e
Not adiabatic, nor frictionless
Ideal
J-T nozzle
Ideal gas piston
Reality

## Slide 18: T-s vs. p-h diagram
p1
p2 < p1

## Slide 19: T-s diagram for nitrogen and lines of constant property
From: USPAS, University of Wisconsin, Madison
Useful for refrigeration cycles with close to isentropic processes
  Turbine expansion,
  Heat exchange at const. pressure
Check the enthalpy curves in the T-s diagram for J-T expansion
Check T-s diagram, lines of constant:
pressure, enthalpy, density and the vapor dome

## Slide 20: T-s diagram for helium and lines of constant property

## Slide 21: T-s diagram for helium
Cryogen | Max. inversion temperature [K]
Helium | 43
Hydrogen | 202
Neon | 260
Air | 603
Nitrogen | 623
Argon | 723
Air can be cooled down and liquefied by J-T expansion from room temperature,
Helium and hydrogen need precooling down to below the inversion temperature by heat exchange or work-extracting expansion (e.g. in turbines).
Source: Refprop®
Published by: International Institute of Refrigeration

## Slide 22: p-h diagram for 3He
Advantages:
Isenthalpic easy to spot
Subcooled liquid region large
Heating the 2-phase region => dh
Q = m * dh
.
.

## Slide 23: Refrigeration cycles

## Slide 24: Open and closed circuits
Cold Box
Cold Box
Cold Box
He gas 300 K
He sat. vapor
@ 4.5 K
He liquid 4.5 K
He liquid
He gas 300 K
Refrigerator
Liquefier
Mixed mode
Adapted from: Cryogenie ses Applications en Supraconductivite, Institut International du Froid.
Balanced heat exchanger due to equal mass flow
Unbalanced heat exchanger by liquid extraction
Unbalanced heat exchanger by e.g. current lead cooling, flow return at ambient temp.

## Slide 25: Joule-Thomson refrigerator
Compressor
Cooler
HEX
Expansion valve
Evaporator
Adapted from: Cryogenie, ses Applications en Supraconductivite, Institut International du Froid.
C - critical point
LP
HP

## Slide 26: Brayton cycle refrigerator
Adapted from: Cryogenie, ses Applications en Supraconductivite, Institut International du Froid.
C - critical point
LP
HP
Compressor
Cooler
HEX
Expansion turbine

## Slide 27: Claude cycle refrigerator
Adapted from: Cryogenie, ses Applications en Supraconductivite, Institut International du Froid.
C - critical point
LP
HP
Compressor
Cooler
HEX
Expansion turbine “warm”
Expansion turbine “cold”
Expansion valve
Brayton cycle
Brayton cycle
J-T cycle

## Slide 28
Process cycle & T-s diagram of LHC 18 kW @ 4.5 K cryoplant
T
s

## Slide 29: Cycles for operation below T=4.4 K
Adapted from: Cryogenie ses Applications en Supraconductivite, Institut International du Froid.
Pump
LP
HP
Ambient temperature pump
Ejector
warm
HP
Ambient temperature ejector
LP
LP*
Ejector at low temperature
Ejector cold
Cold compressor stage
Cold
compressor

## Slide 30: Cycles for operation below T=4.4 K
From: P. Lebrun, The Technology of Superfluid Helium, European Course of Cryogenics, 2019.

## Slide 31: Two-stage Claude cycle

## Slide 32
Once the Entropy had appeared to him
I have seen it.
How the hell did
it look like ??!!
From: Labuhn, Keine Panik vor Thermodynamik, 2011.

## Slide 33
Refrigerator Liquefier

## Slide 34
Refrigerator Liquefier
For refrigerators/liquefiers with the same efficiency:

## Slide 35
Process diagram, LHC refrigerator 18 kW @ 4.5 K
Heat exchangers
Turbines
Adsorbers (remove impurities)
LN2 (cool-down)

## Slide 36: p-h diagram for helium (good for Joule-Thomson stages)
J-T
J-T circuit with precooling:
From: Van Sciver. Helium Cryogenics.

## Slide 37
The effectiveness of J-T expansion
Source: Ph. Lebrun, Cooling with Superfluid Helium

## Slide 38: Summary
Phase diagrams and how to chose the best for your process
Thermodynamic cycles: the reference is Carnot
Isentropic and isenthalpic expansion
Refrigeration cycles Brayton + J-T = Claude
Large scale applications