## Slide 2: Pressure Drop and Heat Transfer in Two-phase flow N2 and CO2
T. Koettig on behalf of the Cryolab team

## Slide 3
Content
Motivation: Thermal shield cooling e.g. of large scale liquid Argon detectors N2 or detector Inner Triplet cooling CO2
Two-phase flow pressure drop
Test stand geometry and features
Pressure drop: measurement results in horizontal, vertical up- and downward orientation N2
Verification of the test set-up by starting in subcooled liquid
Pressure drop and heat transfer on CO2 in horizontal orientation
Summary

## Slide 4
Thermal Shield Cooling of Large Scale Liquid Argon Detectors
3.6 m
3.6 m
3.9 m
3.9 m
19.6 m
neutrino
neutrino
liquid argon
-
-
-
-
-
-
-
+
+
+
+
+
+
+
+
+
+
+
+
+
+
photomultipliers
+
e-
γ
Tsat = 87 K
psat = 1 bar
Tsat = 87 K
psat = 1 bar
liquid argon
thermal shield
polyurethane foam insulation

## Slide 5
Thermal Shield Cooling of Large Scale Liquid Argon Detectors
472 mm
10 mm
4 mm
Fig.: Dimensions of one Al1050A cooling panel
42 panels
2 g/s
boiling nitrogen
Fig.: Arrangement of the cooling panels around the detector
Constraints for the detector cooling thermal shield:
  Outer heat flux of 20 W/m² - foam insulated vessels
  Temperature gradient along shield panel dT< 500 mK
  High purity aluminum 1050A
  Boiling nitrogen as coolant at 87 K

## Slide 6
Thermal Shield Cooling of Large Scale Liquid Argon Detectors
Chart: Temperature in K
| 83.805999999999997 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
argon | 0.68891 | 0.70447 | 0.78897 | 0.8811 | 0.98131 | 1.0901 | 1.2078 | 1.3351 | 1.4723 | 1.6199 | 1.7785 | 1.9485 | 2.1305 | 2.3249 | 2.5323 | 2.7532 | 2.9882 | 3.2377
nitrogen | 1.3687 | 1.5251 | 1.6947 | 1.878 | 2.0757 | 2.2886 | 2.5174 | 2.7626 | 3.0251 | 3.3055 | 3.6046 | 3.923 | 4.2616 | 4.621 | 5.002 | 5.4052 | 5.8316 | 6.2817 | 6.7565 | 7.2566 | 7.7827
Fig.: p-T diagram with vapour pressure curves of Ar and N2
87 K
1 bar
2.8 bar
∆p
∆T

## Slide 7
Two-phase Flow Pressure Drop
Void fraction:
Void fraction versus vapor quality
Void fraction versus mass velocity
x↑  ε↑
G↑  ε↑
in kg/(m2s)
Source: VDI Heat Atlas
0

## Slide 8
Two-phase Flow Pressure Drop
Void fraction:
Void fraction versus vapor quality
Void fraction versus mass velocity
x↑  ε↑
G↑  ε↑
in kg/(m2s)
Frictional pressure drop:
∆pf
x
1
0.85
= 0
at x ≈ 0.85
Frict. press. drop versus vapor quality
Source: VDI Heat Atlas
Slip ratio S introduced
0

## Slide 9
Two-phase Flow Pressure Drop
Void fraction:
Void fraction versus vapor quality
Void fraction versus mass velocity
x↑  ε↑
G↑  ε↑
in kg/(m2s)
Frictional pressure drop:
∆pf
x
1
0.6-0.75
max. at x ≈ 0.6-0.85
Frict. press. drop versus vapor quality
0
0

## Slide 10
Two-phase flow pressure drop
The total pressure drop in two-phase flow is the sum of the gravitational, frictional and momentum pressure drop.
  gravitational pressure drop:
  frictional pressure drop: = – 2ph. multiplier
  momentum pressure drop:
The void fraction is the ratio of the area of the pipe cross-section that is occupied by the vapor phase to the total cross-section.
(p,T), (p,T), S)
slip ratio:
+
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 11
Flow pattern map I
Chart: X
| 8.9999999999999993E-3 | 4.8000000000000001E-2 | 0.1 | 0.28000000000000003 | 0.7 | 2 | 5 | 12 | 70
boundary stratisfy-wavy flow | 1 | 3 | 4.3 | 6 | 6.9 | 6 | 4.6 | 3 | 1
boundary annular-wavy flow | 1.3 | 1.27 | 1.25 | 1.16 | 0.95 | 0.8 | 0.46 | 0.27 | 0.17 | 0.065 | 0.02
boundary wavy-slug flow | 0.17 | 0.065 | 0.02 | 0.001 | 0.0001
boundary annular-bubble flow | 0.18 | 0.5 | 1 | 3 | 4 | 6 | 7 | 9 | 10
boundary bubble-slug flow | 1 | 0.95 | 0.9 | 0.8 | 0.75 | 0.6 | 0.5 | 0.2
process path1 | 0 | 0
Fig.: Flow pattern for horizontal flow
VDI Heat Atlas
Fig.: Flow pattern map according to Taitel and Dukler, VDI Heat Atlas
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 12
Flow pattern map II
Fig.: Flow pattern for vertical flow
VDI Heat Atlas
Fig.: Flow pattern map according to Hewitt and Roberts, VDI Heat Atlas
Chart: il in lb/(ft·s²)
| 1.3 | 5 | 10 | 50 | 60 | 80 | 110 | 200 | 200 | 700 | 900 | 1900 | 5000 | 7000 | 9000 | 10000 | 50000
boundary annular-chaotic flow | 200 | 110 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
boundary chaotic-slug flow | 0.4 | 3 | 5.6 | 6.8 | 20 | 35 | 39 | 44 | 48 | 49 | 50 | 51 | 52 | 52.5
boundary annular-annular wispy flow | 90 | 100 | 200 | 300 | 400 | 600 | 800 | 900 | 2500 | 4300 | 5000 | 7000
boundary slug-bubble flow | 90 | 80 | 70 | 50 | 40 | 20 | 10 | 9 | 3 | 1

## Slide 13
Experimental Set-up
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
LN2
1 bar

## Slide 14
Experimental Set-up
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
Test conditions | 
Pressure (bar abs.) | 2.8
Internal diameter (mm) | 6.0
Mass flow (g/s) | 0.6 – 2.0
Mass velocity (kg/m2s) | 22 - 72
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
LN2
1 bar

## Slide 15: PID (Mass flow control at inlet, pressure control at outlet!)

## Slide 16
Results – Horizontal Orientation
Chart: Vapor quality
| 1.04978702007883E-2 | 4.6921301759706498E-2 | 8.2905198330048405E-2 | 0.11911503679318799 | 0.155014942086311 | 0.19197263402866299 | 0.22751702550995501 | 0.26446625002676699 | 0.30043512233959802 | 0.33632046031082702 | 0.373309788632325 | 0.40883550364701998 | 0.44589425739677502 | 0.48092502912553903 | 0.51814915731503897 | 0.54433954220311598
71.44 kg/(m²s) | 7.6679 | 6.0987 | 7.447 | 6.3111 | 6.8298 | 6.0941 | 7.6793 | 8.1459 | 8.9417 | 11.1126 | 12.406 | 14.2354 | 15.7246 | 17.5038 | 19.2364 | 20.5558
68.61 kg/(m²s) | 5.619 | 5.0199 | 4.867 | 5.587 | 5.8493 | 5.8277 | 6.8716 | 9.1321 | 10.6891 | 12.6061 | 13.9103 | 15.7874 | 16.9158 | 18.3808
59.77 kg/(m²s) | 7.7976 | 6.4009 | 5.0957 | 5.0557 | 4.9302 | 4.9536 | 5.6713 | 6.4692 | 7.9252 | 9.995 | 11.3903 | 12.7332 | 14.0716 | 15.2885 | 16.1411
55.88 kg/(m²s) | 5.7483 | 4.5012 | 4.1759 | 4.4267 | 4.2895 | 4.1686 | 5.1527 | 6.9469 | 7.4849 | 9.7063 | 10.4456 | 11.8839 | 13.3071 | 14.6803
38.55 kg/(m²s) | 4.1229 | 4.1825 | 3.5979 | 3.3329 | 3.1326 | 3.2354 | 3.0556 | 3.2928 | 3.3828 | 3.9917 | 4.7586 | 5.7245 | 6.2814 | 6.6117 | 7.1671 | 7.5717
35.37 kg/(m²s) | 3.4797 | 3.5654 | 3.3841 | 2.9334 | 2.7437 | 3.0442 | 2.9915 | 2.9081
35.01 kg/(m²s) | 3.2986 | 3.1008 | 2.8865 | 3.1672 | 2.4915 | 2.9229 | 2.9043 | 2.8287 | 3.0659
30.42 kg/(m²s) | 2.3526 | 2.4219 | 2.394 | 2.4248 | 2.3909 | 2.5511 | 2.4562 | 2.5709 | 2.6864 | 2.9831 | 3.3041 | 3.5724 | 4.0399
22.64 kg/(m²s) | 3.7715 | 2.523 | 2.3342 | 2.1119 | 1.925 | 2.0221 | 2.0189 | 2.1041 | 2.1843 | 2.2057 | 2.1412 | 2.2355 | 2.2834
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 17: Results – Horizontal Orientation
Chart: Friedel
| 1.04978702007883E-2 | 4.6921301759706498E-2 | 8.2905198330048405E-2 | 0.11911503679318799 | 0.155014942086311 | 0.19197263402866299 | 0.22751702550995501 | 0.26446625002676699 | 0.30043512233959802 | 0.33632046031082702 | 0.373309788632325 | 0.40883550364701998 | 0.44589425739677502 | 0.48092502912553903 | 0.51814915731503897 | 0.54433954220311598
71.44 kg/(m²s) | 7.6679 | 6.0987 | 7.447 | 6.3111 | 6.8298 | 6.0941 | 7.6793 | 8.1459 | 8.9417 | 11.1126 | 12.406 | 14.2354 | 15.7246 | 17.5038 | 19.2364 | 20.5558
71.44 kg/(m²s) - model | 2.2648 | 5.1864 | 7.3015 | 9.1424 | 10.8073 | 12.419 | 13.9006 | 15.3938 | 16.8134 | 18.2047 | 19.6207 | 20.9662 | 22.3581 | 23.6633 | 25.0391 | 25.9993
68.61 kg/(m²s) | 5.619 | 5.0199 | 4.867 | 5.587 | 5.8493 | 5.8277 | 6.8716 | 9.1321 | 10.6891 | 12.6061 | 13.9103 | 15.7874 | 16.9158 | 18.3808
68.61 kg/(m²s) - model | 3.166 | 5.4192 | 7.6313 | 9.5557 | 11.3155 | 13.0109 | 14.7195 | 16.1683 | 17.7094 | 19.2321 | 20.758 | 22.2164 | 23.7227 | 25.1384
59.77 kg/(m²s) | 7.7976 | 6.4009 | 5.0957 | 5.0557 | 4.9302 | 4.9536 | 5.6713 | 6.4692 | 7.9252 | 9.995 | 11.3903 | 12.7332 | 14.0716 | 15.2885 | 16.1411
59.77 kg/(m²s) - model | 1.4246 | 4.2485 | 5.9425 | 7.7132 | 9.3603 | 10.885 | 12.3481 | 13.7437 | 15.1457 | 16.5199 | 18.0618 | 19.2082 | 20.5227 | 21.7788 | 23.0414
55.88 kg/(m²s) | 5.7483 | 4.5012 | 4.1759 | 4.4267 | 4.2895 | 4.1686 | 5.1527 | 6.9469 | 7.4849 | 9.7063 | 10.4456 | 11.8839 | 13.3071 | 14.6803
55.88 kg/(m²s) - model | 1.7354 | 4.2028 | 5.7459 | 7.41 | 8.9168 | 10.3655 | 11.7444 | 13.0837 | 14.4097 | 15.7086 | 16.9648 | 18.2627 | 19.4607 | 20.6388
38.55 kg/(m²s) | 4.1229 | 4.1825 | 3.5979 | 3.3329 | 3.1326 | 3.2354 | 3.0556 | 3.2928 | 3.3828 | 3.9917 | 4.7586 | 5.7245 | 6.2814 | 6.6117 | 7.1671 | 7.5717
38.55 kg/(m²s) - model | 1.1441 | 2.2803 | 3.3374 | 4.2469 | 5.085 | 5.8651 | 6.6009 | 7.4626 | 8.0413 | 8.7325 | 9.4011 | 10.0552 | 10.7025 | 11.3003 | 11.7745 | 12.382
35.37 kg/(m²s) | 3.4797 | 3.5654 | 3.3841 | 2.9334 | 2.7437 | 3.0442 | 2.9915 | 2.9081
35.37 kg/(m²s) - model | 1.0247 | 1.8835 | 2.7059 | 3.4093 | 4.0473 | 4.6495 | 5.2244 | 5.7749
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 18: Results – Horizontal Orientation
Chart: Gronnerud
| 1.04978702007883E-2 | 4.6921301759706498E-2 | 8.2905198330048405E-2 | 0.11911503679318799 | 0.155014942086311 | 0.19197263402866299 | 0.22751702550995501 | 0.26446625002676699 | 0.30043512233959802 | 0.33632046031082702 | 0.373309788632325 | 0.40883550364701998 | 0.44589425739677502 | 0.48092502912553903 | 0.51814915731503897 | 0.54433954220311598
71.44 kg/(m²s) | 7.6679 | 6.0987 | 7.447 | 6.3111 | 6.8298 | 6.0941 | 7.6793 | 8.1459 | 8.9417 | 11.1126 | 12.406 | 14.2354 | 15.7246 | 17.5038 | 19.2364 | 20.5558
71.44 kg/(m²s) - model | 0.86869 | 1.5169 | 2.333 | 3.3124 | 4.4269 | 5.7176 | 7.0882 | 8.6455 | 10.2864 | 12.0423 | 13.9754 | 15.9453 | 18.1156 | 20.2696 | 22.6602 | 24.3982
68.61 kg/(m²s) | 5.619 | 5.0199 | 4.867 | 5.587 | 5.8493 | 5.8277 | 6.8716 | 9.1321 | 10.6891 | 12.6061 | 13.9103 | 15.7874 | 16.9158 | 18.3808
68.61 kg/(m²s) - model | 0.97764 | 1.5792 | 2.5225 | 3.6584 | 4.9667 | 6.4731 | 8.2322 | 9.909 | 11.8737 | 13.9932 | 16.2891 | 18.6396 | 21.2209 | 23.7799
59.77kg/(m²s) | 7.7976 | 6.4009 | 5.0957 | 5.0557 | 4.9302 | 4.9536 | 5.6713 | 6.4692 | 7.9252 | 9.995 | 11.3903 | 12.7332 | 14.0716 | 15.2885 | 16.1411
59.77 kg/(m²s) - model | 0.5988 | 1.165 | 1.8026 | 2.7453 | 3.8908 | 5.1858 | 6.6383 | 8.211 | 9.9701 | 11.8639 | 14.1829 | 16.0353 | 18.285 | 20.5417 | 22.8766
55.88 kg/(m²s) | 5.7483 | 4.5012 | 4.1759 | 4.4267 | 4.2895 | 4.1686 | 5.1527 | 6.9469 | 7.4849 | 9.7063 | 10.4456 | 11.8839 | 13.3071 | 14.6803
55.88 kg/(m²s) - model | 0.58445 | 1.1387 | 1.7526 | 2.6774 | 3.7618 | 5.0279 | 6.4338 | 7.9824 | 9.6888 | 11.5235 | 13.4472 | 15.5803 | 17.6638 | 19.783
38.55 kg/(m²s) | 4.1229 | 4.1825 | 3.5979 | 3.3329 | 3.1326 | 3.2354 | 3.0556 | 3.2928 | 3.3828 | 3.9917 | 4.7586 | 5.7245 | 6.2814 | 6.6117 | 7.1671 | 7.5717
38.55 kg/(m²s) - model | 0.32584 | 0.53705 | 0.87917 | 1.3025 | 1.8058 | 2.3743 | 2.9995 | 3.8412 | 4.4726 | 5.296 | 6.1645 | 7.0816 | 8.0513 | 8.992 | 9.7544 | 10.704
35.37 kg/(m²s) | 3.4797 | 3.5654 | 3.3841 | 2.9334 | 2.7437 | 3.0442 | 2.9915 | 2.9081
35.37 kg/(m²s) - model | 0.37773 | 0.79638 | 1.3083 | 1.8086 | 2.2997 | 2.7886 | 3.2744 | 3.7546
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 19
Results – Horizontal Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 20
Vertical Upward Orientation

## Slide 21
Results – Vertical Upward Orientation
Flow is always in chaotic regime
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 22
Vertical Downward Orientation

## Slide 23
Results – Vertical Downward Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 24: Verification of the set-up
Enter the two-phase range from the liquid phase (subcooled)
Monitor the change in pressure drop
Monitor the temperature behaviour single phase to saturation conditions

## Slide 25
Experimental Set-up
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
Test conditions | 
Pressure (bar abs.) | 2.8
Internal diameter (mm) | 6.0
Mass flow (g/s) | 1.44
Mass velocity (kg/m2s) | 51
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
LN2
1 bar

## Slide 26
Results – Verification Test
Temperature inlet

## Slide 27: CO2 two-phase flow in mini channels
Pressure drop and heat transfer study in a horizontal mini-channel as a function of:
  vapor quality
  mass flux
  heat flux
  psat and Tsat

## Slide 28
CO2 two-phase flow pressure drop
d=1.4 mm
From: VDI Waermeatlas Hbb4, 2006
S => SW
Intermitt.
Annular
Dry-out
Mist

## Slide 29
CO2 two-phase flow - Pressure drop

## Slide 30
CO2 two-phase flow - Pressure drop
From: D. Helmer, Investigation of Heat Transfer and Pressure Drop Phenomena of CO2 in Two Phase Flow
100
10
Pressure drop and or heating two-phase flow is cooling!

## Slide 31
CO2 two-phase flow - Heat transfer (heat and mass flux dep.)
d=1.4 mm
Mass flux dep. at low heat flux
Mass flux dep. at high heat flux

## Slide 32
CO2 two-phase flow - Heat transfer (temperature dependency)
d=1.4 mm
Temperature dep. at low heat flux
Temperature dep. at high heat flux

## Slide 33
Summary
Two phase flow is special, remember the cooling effect by Δp(G) or Δp(q)!
Pressure drop at x~0.7-0.85 can be much higher than in gas or liquid phase
Deviation in vertical upward orientation of the models for small vapor quality
Models fail to predict pressure drop for vertical downward direction
First bubbles create buoyancy effect that overcomes gravitational influence
Consider the dry out and the sudden decrease in heat transfer for x>~ 0.7
Design for sufficient flow speed to avoid phase separation => syphons/instabilities
Parallel channels => tuning of the inlet restriction to 100 % pressure drop of the heated section