## Slide 2: Forced Convection Flow Modelling
B. Naydenov

## Slide 3: Content
Convection
Numerical Model
Single-phase flow
Supercritical flow
Two-phase flow
Results

## Slide 4: Convection

## Slide 5: Convection - Heat transfer
Heat transfer by mass motion of a fluid
Common in cryogenics:
  Liquid baths
  Transfer lines
  Heat exchangers
  Capillaries
Enable remote cooling systems
Heat transfer rate (and pressure drop) depend on:
  Fluid properties
  Convection type
  Flow regime
  Flow state
Notes: Remote cooling systems could also be achieved just by means of conduction or radiation, but that would limit them in different aspects, either the mechanical decoupling would fail, or the transported cooling power would be too small (big losses).

## Slide 6: Convection - Types
http://www.mhhe.com/engcs/mech/cengel/notes/ConvectionHeatTransfer.html
Forced Convection | Natural Convection
Driven by an external mechanism | Driven by buoyancy
- Less reliable | + Reliable
+ Enhanced heat transfer () Gases: 25-250 W/(m2K) Liquids: 50-20000 W/(m2K) | - Lower heat transfer Gases: 2-25 W/(m2K) Liquids: 50-1000 W/(m2K)
Forced Convection | Natural Convection
Driven by an external mechanism | Driven by buoyancy
- Less reliable | + Reliable
 | - Lower heat transfer Gases: 2-25 W/(m2K) Liquids: 50-1000 W/(m2K)
Notes: External pump causes a pressure difference.

## Slide 7: Convection – Types – Natural Convection
https://cms.cern/detector
European Graduate Course in Cryogenics 2010
1.5 kW @ 4.5 K cryoplant
Example 1: CMS solenoid cooling
He thermosyphon loop
Notes: 100 m depth

## Slide 8: Convection – Types – Forced Convection
https://atlas.cern/Resources/Schematics
Les JournéesThématiques AFF-CCS – G. Passardi
Example 2: ATLAS toroid cooling
Barrel toroid
End-cap toroid
Solenoid
Notes: Centrifugal pumps forcing the circulation of 1200 g/s saturated He flow.

## Slide 9: Convection - Regimes
https://www.sfu.ca/~mbahrami/ENSC%20388/Notes/Forced%20Convection.pdf
Regime
Laminar: smooth and streamlined flow (10 – 1000 W/m2K ) At Re < 2320 (circular duct) or < 5x105 (flat plate)
Turbulent: disordered flow with velocity fluctuations. At Re > 2320 (circular duct) or > 5x105 (flat plate) ↑ friction force, ↑ (20 – 20000 W/m2K)
Regime
Laminar: smooth and streamlined flow (10 – 1000 W/m2K ) At Re < 2320 (circular duct) or < 5x105 (flat plate)
Notes: The intense mixing of the fluid in turbulent flow enhances heat and momentum transfer between fluid particles.
Critical Reynolds number

## Slide 10: Convection - States
Case | [W/m2K]
Free convection | Gases: 2-25 Liquids: 50-1000
Forced convection | Gases: 25-250 Liquids: 50-20,000
Supercritical flow forced convection | 1000-50,000
Two-phase flow convection | 2500 – 100,000
Case | 
Free convection | Gases: 2-25 Liquids: 50-1000
Forced convection | Gases: 25-250 Liquids: 50-20,000
Supercritical flow forced convection | 1000-50,000
Two-phase flow convection | 2500 – 100,000
He critical point
(5.2 K – 2.23 bar)
Two-phase flow
Supercritical flow
Gas
Liquid
The friction factor varies as well
REFPROP
Saturation line
Notes: External pump causes a pressure difference.

## Slide 11: Numerical Model
Cooling Interface

## Slide 12: Forced Convection - Modelling
Convection: heat transfer by mass motion of a fluid.
Fluid dynamics involved → Navier-Stokes equations need to be solved.
Mass: Continuity equation – mass conservation
Momentum: Newton’s Second Law equation – momentum conservation
Energy: First Law of Thermodynamics equation – energy conservation
Notes: Momentum equation has
  surface forces (pressure force and viscous force) and
  body forces (massic force and electromagnetic force).
Energy equation is basically U = Q (heat flux) – W (work of viscous forces). Work of mass forces has been also neglected here.
Electromagnetic energy and forces have been neglected here.

## Slide 13: Forced Convection - Modelling
Simplifications:
Steady-state
Body forces are neglected since the differences in height are low:
Viscous forces work negligible:
The difference of kinetic or potential energy is very small compared to the heat ﬂux:

## Slide 14: Forced Convection - Modelling
Simplified equations:
Mass: Continuity equation
Momentum: Newton’s Second Law equation (F = ma)
Energy: First Law of Thermodynamics equation
Notes: External pump causes a pressure difference.

## Slide 15: Forced Convection – Capillary modelling
Finite Volume Method (FVM) discretisation approach:
Conduction: cell-centred control volume
Convection: face-centred control volume
wall
Symmetry Axis
∆x = L/N
Flow
inlet
t
[W/m2]
= 0
Notes: FVM, FDM and FVM: https://knowledge.autodesk.com/support/cfd/learn-explore/caas/CloudHelp/cloudhelp/2014/ENU/SimCFD/files/GUID-12A9AED8-2047-4D3A-BC80-82BE9CF47517-htm.html
FVM is very suitable for the conservation laws.
On a first iteration, heat flux is constant along the capillary. Could be refined later.

## Slide 16: Forced Convection – Capillary modelling
Iterative solver procedure:
Solve fluid
  Initial properties distribution assumed.
  Solving cell by cell, until all the capillary is calculated.
Solve solid with the updated fluid properties.
Check convergence criteria for both fluid and solid.
  If not passed, go back to 1.
  If passed, save values and finish.
Open points → how to deal with and ?
Depends on the flow regime and the flow state.
Notes: FVM, FDM and FVM: https://knowledge.autodesk.com/support/cfd/learn-explore/caas/CloudHelp/cloudhelp/2014/ENU/SimCFD/files/GUID-12A9AED8-2047-4D3A-BC80-82BE9CF47517-htm.html
FVM is very suitable for the conservation laws.

## Slide 17: Single-phase flow

## Slide 18: Forced Convection – Single-phase flow inside a circular tube
and are evaluated at the mean cell temperature, with the help of a thermophysical library (CoolProp or Hepak).
depends on the flow regime and is obtained with empirical Nusselt correlations.
  Laminar flow ( →
  Turbulent flow ( → (Dittus-Boelter)
depends on the flow regime and the surface rugosity.
  Laminar flow ( → (Fanning)
  Transition flow ( → (Blasius)
  Turbulent flow ( → (McAdams)
Notes: # # also, Johannes Correlation (1972) https://uspas.fnal.gov/materials/10MIT/Lecture_3.2.pdf
# Nu_m = 0.0259 * Re_m ** (4/5) * Pr_m ** (2/5) * (Tt[i]/Tm) ** (-0.716)

## Slide 19: Forced Convection – Single-phase flow inside a circular tube
https://en.wikipedia.org/wiki/Moody_chart
Common confusion between Fanning and Moody (aka Darcy-Weisbach) friction factors. If wrongly used, factor 4 difference in pressure drop calculations.
Recommendation: use Fanning for NS equations and Moody for an isolated pressure drop calculation.
Notes: # # also, Johannes Correlation (1972) https://uspas.fnal.gov/materials/10MIT/Lecture_3.2.pdf
# Nu_m = 0.0259 * Re_m ** (4/5) * Pr_m ** (2/5) * (Tt[i]/Tm) ** (-0.716)

## Slide 20: Supercritical flow

## Slide 21: A comparison of heat transfer to helium
Higher Re increases heat transfer
For higher ΔT nucleate boiling reaches SC forced flow
Kapitza at 1.9 K is not that bad
RKap dominant only below 1 K
Source: V. Arp, Adv. Cryogenic Eng., Vol. 17, pp. 342.
“ “
Notes: Big property change over a small temperature difference.
Similar behavior is expected for any fluid.

## Slide 22: Particularities of Supercritical flow (SCF)
Properties change a lot near the critical point. Example for He:
He critical point → 5.19 K and 2.24 bar
Heat capacity peak defines the pseudo-critical point at each pressure.
Fluid changes from liquid-like to gas-like.
Big change of properties over small temperature difference.
The density changes could lead to unstable behaviour.
Source: V. Arp, Adv. Cryog. Eng., Vol. 17, 342
or maximum specific heat line
Notes: Big property change over a small temperature difference.
Similar behavior is expected for any fluid.

## Slide 23: Particularities of Supercritical flow (SCF)
Properties change a lot near the critical point. Example for He:
Source: Vvaghela, Forced flow cryogenic cooling in fusion devices: A review
From: Smith, A Review of Heat Transfer to Helium I
Notes: Big property change over a small temperature difference.
Similar behavior is expected for any fluid.

## Slide 24: Particularities of Supercritical flow (SCF)
Source: H. Ogata, S. Sato, Proc. ICEC 4, Eindhoven, (1972), 291
Increase of heat capacity leads to an improvement of the heat transfer coefficient.
↑pressure →↓ peak
↑heat flux →↓ peak
The improvement is mainly near the critical point (transposed critical line).
α
α
α
α
Heat transfer coefficient to supercritical forced flow of Helium:
Mass flow =0.17 g/s, as fct. of temperature pressure and heat flux.
3 bar, 5.6 K
5 bar, 6.4 K
8 bar, 7.5 K
15 bar, 9.7 K
Simulation made with
Nu=0.023 * Re0.8*Prmin
Notes: Big property change over a small temperature difference.
Similar behavior is expected for any fluid.
Increasing the flux reduces the high region in the fluid. As the temperature difference is increased, the proportion of the flow experiencing this high specific heat shrinks, and the heat transfer coefficient is reduced.
Improvement is valid mainly for high mass fluxes forced convection cases. For mixed or free convection, the heat transfer could also worsen depending on the orientation.
Big property change over a small temperature difference.
Similar behavior is expected for any fluid.
Increasing the flux reduces the high 𝐶_𝑝 region in the fluid. As the temperature difference is increased, the proportion of the flow experiencing this high specific heat shrinks, and the heat transfer coefficient is reduced.
Improvement is valid mainly for high mass fluxes forced convection cases. For mixed or free convection, the heat transfer could also worsen depending on the orientation.

## Slide 25: Forced Convection – Supercritical flow inside a circular tube
Heat transfer correlation requires modifications to account for the property variations. The most complete one was found to be the one from Jackson:
[1] Jackson, J. D. et al. Heat transfer to supercritical pressure fluids, 1975 (referred from https://thermopedia.com/content/1173/)
Where w refers to conditions at the wall, and b to the bulk of the fluid. is defined as:
Finally, is a function on and (pseudo-critical temperature). [1]
Notes: F is more a function of regime and rugosity.
Forced Convection in the Absence of Buoyancy

## Slide 26: Forced Convection – Supercritical flow inside a circular tube
and are evaluated in the same way as the single-phase flow case.
is obtained from:
  Jackson, if conditions are close to the critical point.
  Dittus-Boelter, otherwise.
Helium conditions | Correlation
4.2 K < T < 9 K 2.24 bar < p < 5 bar | Jackson
T > 9 K p > 5 bar | Dittus-Boelter
Helium’s critical point → 5.19 K and 2.24 bar
Notes: Helium limits for Jackson are personal choice. Tested to use Jackson always if SC but it didn’t make a big change compared to Dittus Boelter.

## Slide 27: Two-phase flow

## Slide 28: Particularities of Two-phase flow (TPF)
Why TPF?
  Cryogens are volatile and are often distributed near saturation conditions.
  Attractive heat transfer rate.
  Constant temperature.
He critical point
(5.2 K – 2.23 bar)
Two-phase flow
Supercritical flow
Gas
Liquid
REFPROP
Saturation line
TPF implications:
  Mostly an empirical subject due to its complexity.
  Variables that affect it: mass flow rate, temperature, pressure, orientation and phase change.
  Instabilities should be assessed.
Notes: Cryogens are volatile and are often distributed near saturation conditions.
Two phase flow instabilities are undesirable as they can result in mechanical vibrations and system control problems, affect normal operation, restrict operating parameters and influence system safety.

## Slide 29: Particularities of Two-phase flow (TPF)
Flow patterns in a horizontal pipe:
Quibén, Jesús. (2005). Experimental and analytical study of two-phase pressure drops during evaporation in horizontal tubes. 10.5075/epfl-thesis-3337.
Notes: Adiabatic: pattern depends on mass flow rate, vapour quality, geometry of the capillary.
Diabatic: with uniform heat throughout the pipe.

## Slide 30: Particularities of Two-phase flow (TPF)
Flow patterns in a vertical pipe:
D. Schmid. (2022) Flow pattern observations and flow pattern map for adiabatic two-phase flow of carbon dioxide in vertical upward and downward direction. 10.1016/j.expthermflusci.2021.110526

## Slide 31: Methods of analysis – TPF models
How to adapt the numerical model to a TPF?
Homogeneous flow model: assumes that the two phases travel at equal velocities and mix well. Hence, they are treated as one phase, with averaged properties.
Separated flow model: separates the flow in two differentiated parts. Slip velocities and mass transfer between the phases need to be accounted for.
Flow pattern model: it is necessary to know the flow pattern and solve the equations accordingly per pattern forming in the tube. Flow pattern maps are used.
Notes: Homogeneous flow is accurate for bubbly flow and mist flow. Especially not accurate for stratified flow.

## Slide 32: Methods of analysis – TPF model
Approach: homogeneous flow model combined with a flow pattern map.
- Cheng 2007. New prediction methods for CO2 evaporation inside tubes: Part I – A two-phase flow pattern map and a flow pattern based phenomenological model for two-phase flow frictional pressure drops
- Cheng 2008. New prediction methods for CO2 evaporation inside tubes: Part II—An updated general flow boiling heat transfer model based on flow patterns
Inside the iterative numerical model, at each cell:
The pattern of the flow is identified. It is a function of the heat flux, temperature, mass flux, geometry of the capillary and vapour quality.
The heat transfer coefficient is determined using the model for the obtained pattern.
The pressure drop is determined using the model for the obtained pattern.
Density is averaged in the following way:
  Where is the vapour quality (or flow quality) defined as:
As for the heat transfer coefficient and the friction factor (pressure drop), a flow pattern map adapted from CO2 (Wu) is used (See Cheng Part I and II).
Notes: The new density is used to get the speed of the flow – which is used to calculate the pressure.
flow pattern based phenomenological model. A phenomenological study explores what people experienced and focuses on their experience of a phenomena.
With this approach, the iterative model can be solved now.

## Slide 33: Methods of analysis – TPF model
Example flow pattern map for Helium:
Dryout represents the transition between annular and mist flow.
(10.5075/epfl-thesis-3337)
Notes: Mist onset is extracted from the dryout completion (which means the wall remains completely dry).

## Slide 34: Methods of analysis – TPF model
Evolution of properties along the capillary:
Distance along capillary [m]

## Slide 35: Summary – regimes comparison
(a) Fluid temperature and (b) pressure drop variation along the capillary CIF for various flow conditions. CIF inner diameter is 3 mm, heat load is 3 W (distributed), = 200 mg/s, = 4.5 K.

## Slide 36: Summary – regimes comparison
Influence of the capillary’s diameter on (a) the difference between the average capillary and fluid temperatures, and (b) the total pressure drop for different flow conditions. CIF length is 10 m, heat load is 3 W (distributed), = 200 mg/s, = 4.5 K.

## Slide 37: Conclusions
Convection relevance.
1D capillary numerical model solved for convection and conduction.
Convection part accounts for:
  Single-phase flow: traditional approach
  Supercritical flow: modification near the critical point
  Two-phase flow: new approach mixing the classic homogeneous model with a flow pattern map.
Two-phase flow pattern map adapted from CO2 for horizontal channels.
  Results to be verified in experimental campaigns.

## Slide 39: Particularities of Supercritical flow (SCF)
http://indico.ictp.it/event/a10196/session/19/contribution/14/material/0/0.pdf
Increasing the heat flux reduces the high region in the fluid.

## Slide 40: Methods of analysis – TPF models
Example flow pattern map for Helium:
Capillary: 3 mm / 10 m
Heat load: 3 W
Mass flow rate: 200 mg/s
Notes: - dryout : when the heat flux exceeds a critical value (CHF – critical heat flux) the flow pattern may reach the dryout conditions (thin film of liquid disappears)

## Slide 41: TPF DWO instabilities
Ishii stability map:
Notes: https://folk.ntnu.no/cadorao/TPFlowInstabilities.html
Pressure drop oscillations https://www.youtube.com/watch?v=TYJcEgQAZ38
Density wave oscillations https://www.youtube.com/watch?v=AKuddK7du6Y

## Slide 42: TPF and SC DWO instabilities – Stability map