## Slide 1
June 2025
X. Pons on behalf of the DT-DI Section
Detector Technology Group Meeting
Detector Interface Section
Magnet Services

## Slide 2
Detector Interface Section
Magnet
Support
Detector
Support
Data Acquisition Support
The Detector Interface provides hardware and software support in control, safety and data acquisition systems for experiments infrastructure.
Experiment
Data

## Slide 3
Detector Interface Section – Magnet Services
EP-DT has a long tradition supporting the experimental magnets
Since the initial design phases of the ATLAS and CMS magnet control in the 90’s with the old TA3 group
DT-DI has been responsible of the Magnet Control Project (MCP) for the LHC Experimental Magnets
Later, during the operation of the LHC, and agreement was established with the experiments to define the DT-DI’s support in terms of operation and maintenance.
This agreement also included the support for the Detector Safety Systems (DSS)

## Slide 4
LHC Experimental Magnets
1.1 T

## Slide 6
DT-DI is also providing support to the: Compass, AeGis, Vertex 1 and 2, M1 and M2 and T2K (Old UA1) magnets

## Slide 7
Prof. H Ten Kate: CERN Accelerator School on Superconductivity for Accelerators, Erice 2013
Why a Magnet Safety System?

## Slide 8
Why a Magnet Safety System?
LHC Dipole interconnection September 2008

## Slide 9
Why a Magnet Safety System?

## Slide 10
Magnet Control Project (MCP 2025)
ATLAS
CMS
ALICE
LHCb
Giulio Malaguti
Laurent Deront
Maciej Ostrega
Giulio Malaguti
Jarl Pettersen
MSS Software Experts
Sylvain Ravat
Valentina Reynaud
MCS Software Experts
Sylvain Ravat
Maciej Ostrega
MCS/MSS Hardware Experts
Laurent Deront
Xavier Pons
Workshop / FSU
Marc Carrichon
Murat Dinger
Bayram Dinger
Jerome Bourachot

## Slide 11
Maciej Ostrega
G. Malaguti
J Pettersen
X Pons
K Barth
(ALICE)
A Meynet
(CMS)
J Vizdal
(ATLAS)
L Roy
(LHCb)

## Slide 12
LS3 Activities
1- Replace the battery charger of the MSS and QH
2- Replace the batteries
3- MDS: New updated MDS
4- MSS Interfaces:
- Update of the DI Interfaces
- Updated of the DI/DO Interfaces
- VAM
5- Replace the cRIO-FPGA + modules
1- To install the diffusion pumps
2- To Install the DC power for these diffusion pumps =>
2.1 New DC power supply rack
2.2 New EXD6 power cabinet
3- Maintenance of the primary pumps (replace by new ?)
4- Maintenance of the diffusion pumps (last year before run)
5- Replacement of the Vacuum gauges
Vacuum Activities
VAM – Quench detection board
ATLAS new diffusion pump

## Slide 13
OLD DSS
Siemens S7-300
New DSS
Siemens S7-1500
About Detector Safety System
Recently DT-DI established an agreement with the LHC Experiments and in collaboration with BE-ICS in order to provide support for the LS3 upgrade of the Detector Safety System (DSS) to the new version DSS2
Basically, consist in a production of 50 racks with the new redundant PLC based on Siemens S7-1500 and the replacement of all the connections

## Slide 14
Thank you for your attention, questions?

## Slide 15
Backup

## Slide 16
Introduction 2. Why a Magnet Safety System?
Prof. H Ten Kate: CERN Accelerator School on Superconductivity for Accelerators, Erice 2013
DT-DI MSS is a quench protection system

## Slide 17: MSS2 Hardware Architecture Overview
ANALOGUE INPUT INTERFACE BOARD
Dual Analogue Input Range
Multiple signal range, hardware programmable range:
x1, x10, x100, x1000
set by DIP switch.
Signal isolation 1500Vrms.
Power supply circuit isolated 3 kV by DC-DC converter between channel - channel-FPGA_AI - Power_Supply
Each channel has its own selectable current source by DIP_SWITCH.
0.01 mA, 0.1 mA, 1mA, 10 mA.
Optional low pass filter
Optional gain and offset adjustment
Time and level discrimination done at FPGA level
EDMS
MSS2 Analogue Input interface board

## Slide 18: MSS2 Hardware Architecture Overview
MSS2 Main crate
  Following L. Deront design
  6U crate size for 19’ rack assembly compatible with all MSS
  cRIO FPGA installed in the front side
  Input/Output Interface board in the back side
  Redundant Power supply
MSS2 Prototype
MSS2 cRIO crate. Front Side view
MSS2 cRIO crate. Front Back Side view

## Slide 19
WINCC Dataserver cs-ccr-mads3
USA15 EXD6 power control
UX15 Vacuum Field
USA15 Schneider Vacuum PLC
Remote Access
Terminal Server
Automatic Notification System
CERN TN
Modbus Driver
ANS
Hardwired
Piquet
CCC
Hardwire
Hardwire
Hardwire to UX15 Level 0 Patch Panel
Hardware Vacuum Control system Layout
USA15 Schneider VHS PLC
CERN TN
Modbus Driver
Hardwire
Hardwire
USA15 Green Zone 2 MW power distrib
Orange bands
On BT vessel
ENEL TWIDO
Monitoring PLC
CERN TN
IOScanning
VHS Trigger, Hardware
Turbo

## Slide 20
Upgrade approach
CPU
X3 Remote I/O
Remote I/O
Remote I/O
Vacuum
VHS
EXD6
CPU2
Turbo
CPU3
USA15
USA15
USA15
UX15
USA15
USA15
USA15
WINCC Dataserver cs-ccr-mads3
WINCC
To split the Turbo Pump system in an independent and redundant control system
With an independent WINCC project

## Slide 21
9 inputs RTD, PT100, PT1000
For Siemens 6ES7531-7PF00-0AB0
45 mm wide
8 inputs 0-10V or 4..20mA
Possible to mix
45 mm wide

## Slide 22
32 Digital Inputs – logic 0-24V
Optocoupled Toshiba TLP627M (=DSS)
Input overvoltage protection TVS 33V
Status LED for each DI
72 mm wide
Optocouplers individually replaceable
Module fuse protected
For Siemens 6ES77521-1BL00-0AB0

## Slide 23
I/O Interfaces – Digital Output
32 Digital Output – Relay with COM, NO, NC contacts
Key Switch Override function, closes all the relays
Status LED for each DO
72 mm wide
Design finished,
Both Digital Input and Output interfaces are on endurance test
They require a new version wit cables entering from top

## Slide 24: FD on 17.10.2024

## Slide 25: FD on 17.10.2024
DSS alarm at 20:14:57.
FD took place after trigerring an SD, within 3s.
Magnet current was 16977 A (3.55T at IP).
CPs open command at 20:15:32.030
FD at 8:15:32.100
CRs open at 20:15:33.905 after quench detection on DT3a
CRs close command at 20:15:30.030