## Slide 1
Maria Cristina Arena, A. Bouzaiene, M. Busato, D. Galassi, R. Guida, S. Juks, B. Mandelli, G. Rigoletti, P. Vanslambrouck, M. Verzeroli
Optimization of GHG usage for particle detectors

## Slide 2: Use of fluorinated gases at the CERN LHC
R134a
SF6
CF4
C4F10
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 3: GHGs emissions at CERN
https://doi.org/10.25325/CERN-Environment-2023-003
Fluorinated compounds represent the 78% of total Organization’s emissions which will be reduced by 28% by the end of RUN 3 (wrt 2018)
R134a  emissions reduced by 25% during RUN3 thanks to the operation of the CMS R134a recovery plant & new 30% CO2 ATLAS RPC gas mixture
CF4  emissions reduced by 20% thanks to the increase of recuperation efficiency of CMS CF4 recovery plant.
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 4: F- EU regulations
New EU legislation of 2024 is strongly limiting the use of these gases through different approaches:
Promoting the use of more eco friendly alternatives
Controlling and preventing emissions
Reducing the availability of hydrofluorocarbons
Sharp reduction in available HFC supply quota  spike of prices
Higher prices with lower demand due to transition to low GWP alternatives
It will become harder and more expensive to get, mainly used for servicing old systems until fully phased out.
Gas Team strategies to reduce GHG emissions started even before the first EU legislation of 2014!

## Slide 5: EP-DT-FS Gas Team
The Gas systems team is responsible for
Design and construction of gas systems for particle detectors at CERN
Operation, maintenance and upgrades of gas systems installations
Provide support to analyse gas samples
More than 30 large gas systems installations
Industrial grade plants to control gas to the detectors (mixture, temperature, pressure, flow, etc.)
Modular design: increase construction efficiency, decrease operational costs
Each installation consists of
~10-102 sensors
~few to 102 actuators
~2-3 km of pipes
Tour Eiffel 324 m
All gas systems racks 500-600 m
Burj Khalifa 828 m
Schematic view of the LHC gas systems
ATLAS RPC gas system in surface gas room
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team
https://doi.org/10.1007/978-981-13-1313-4_19

## Slide 6: Layout of LHC gas systems
GAS MIXER
EXHAUST
DETECTOR
EXHAUST
GAS MIXER
DETECTOR
OPEN LOOP  100% of gas loss
GAS RECIRCULATION  ~ 10% of gas loss
RECOVERY PLANT
GAS MIXER
DETECTOR
EXHAUST
GAS RECUPERATION  0% of gas loss*
*due to gas system operation
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 7: Strategies to reduce GHGs emissions at CERN
Strategies
Optimization of gas system technologies
Gas recirculation
Particular attention to operation
Improved control and monitoring
Gas recuperation systems
Pressure swing
Membrane separation
Distillation
Alternative gases
To C2H2F4
To SF6
To CF4
Disposal and abatement
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 8: Gas recirculation systems

## Slide 9: Why not 100% of recirculation?
Some detectors cannot work at 100% of gas recirculation due to their air/H2O permeability (NOT leaks!)
This means that these components would be accumulated in the gas mixture leading to detector ageing or lower performances!
Many gas detectors have been validated to work at 90% of recirculation fraction due to the formation of impurities in the gas loop, such as F-, which can cause long-term ageing effects!
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 10: Gas recirculation
Gas recirculation represents the first strategy to mitigate GHG emissions for particle detection:
For detectors’ volumes between 1 and 100 m3
16 recirculating gas systems working 24/24
PROS
Gas consumption reduced up to 90-100% (depending on the detector requirements)
System paid back thanks to the gas saved
CONS
Higher complexity of the system
Analyses required to monitor the quality of recirculated gas
GAS MIXER
DETECTOR
EXHAUST
GAS RECIRCULATION  ~ 10% of gas loss
ATLAS RPC gas system in surface gas room
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 11: Optimization of gas system technologies
As slow as possible opening at input
New modules with regulation valves
New restart procedure
Additional regulation valves
Two sets of PID
Pressure regulation by using Detector pressure or “reference volumes”
with new valve
Minimize detector pressure/flow fluctuation to cope with observed inborne fragility of detector components  From < 1 mbar to ~ 0.1 mbar not an easy challenge
All upgrades required dedicated R&D, development of components, commissioning, … and today operation is more complex
Our operating conditions often have no equivalents in the industrial domain!
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team
https://doi.org/10.1016/j.nima.2023.168444

## Slide 12: Analyses to monitor gas recirculation systems
Monitoring systems
Potentiometric analysis to monitor F- production in LHC systems
µGC analyses
Online monitoring setups
Infrared analyser
SWPC
Operating these systems is challenging & impurities are formed in the gas loop (e.g. F-)  filtering and monitoring systems are crucial!
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team
https://doi.org/10.1016/j.nima.2025.170515
https://doi.org/10.1088/1748-0221/14/09/C09006

## Slide 13: Small and micro recirculating systems
LHC gas system
Micro recirculation system
Target  Small laboratory gas detector setups (flushing of few l/h)
Proposal  micro gas recirculation system
As with gas systems, gas is pumped around in closed loop
Requirements
  For detector volumes up to 100L
  Compact and portable: fits on a desk / in a box
  Modular: every setup has different needs (optional purifier, flow monitoring, analysers etc.)
  Starting price ~ O(10³) CHF
  Easy to build, use and maintain
  Simple control and monitoring
Small recirculation system
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team
https://doi.org/10.1016/j.nima.2023.168095

## Slide 14: Gas recuperation systems

## Slide 15: Gas recovery systems for fluorinated gases
Due to air accumulation in the gas mixture, some detectors cannot work with a 100% recirculated fraction
Usual recirculation fraction of 90% (detector requirements) → 10% sent to the exhaust
In some cases, this gas is sent to recovery plants where the GHG is separated from the other components, stored and then re-injected in the mixer through a dedicated line
RECOVERY PLANT
GAS MIXER
DETECTOR
EXHAUST
GAS RECUPERATION  0% of gas loss*
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team
https://doi.org/10.1088/1748-0221/15/10/C10028

## Slide 16: Separation techniques - overview
Ability of a membrane to separate two molecules
MEMBRANE SEPARATION
Driven by partial pressure gradient
Depends on membrane nature & permeability
Affected by solubility and diffusivity
ADSORPTION (PSA/TSA)
PSA  pressure changes for regeneration
TSA  heat for regeneration
Vacuum prevents overheating
DISTILLATION
Based on boiling point differences
Lighter components  vapor phase
Heavier components  liquid phase
MEMBRANE SEPARATION
CF4  CMS CSC, LHCb RICH2
ADSORPTION (PSA/TSA)
CF4  CMS CSC
DISTILLATION
R134a  CMS RPC
C4F10  LHCb RICH1
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 17: CMS CSC recovery system for CF4
First plant for CF4 warm adsorption, non-standard gas system
CSC gas mixture: Ar/CO2/CF4 = 40/50/10 or 40/55/5
System is fully controlled by software
MEMBRANES
CO2 ADS.
CF4 ADS.
BUFFER
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 18: CMS CSC recovery system for CF4
Phase 1  CO2 separation
CO2 / Ar / CF4 = 55 / 40 / 5 or 50 / 40 / 10 + 1% of N2
Feed
100 l/h
CO2 / Ar / N2 = 60 / 39 / 1
Permeates
94-88 l/h
Retentates
6-12 l/h
CF4 / Ar / N2 / CO2 = 83 / 15 / 2 / 500 ppm
Phase 2  Adsorption of remaining CO2
From Membrane’s Retentates
To Phase 3
CF4 / Ar / N2 = 85 / 5 / 15
CO2 adsorption with zeolite 4A
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 19: CMS CSC recovery system for CF4
Phase 3 & 4  CF4 adsorption, extraction and storage
From Phase 2
CF4 / Ar / N2 = 92 / 7 / 1
CF4 Storage Battery
Vacuum
Patm
Phase 1 (Patm to -400 mbar): Ar and N2 venting
Phase 2 (-400 mbar to vacuum):
CF4 extraction
To CSC mixer
CF4 adsorption with zeolite 13X
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 20: CMS CSC recovery system for CF4
Efficiency mean value: 70% in the period January-November 2024
In 2024, out of 495 m3 of CF4 injected into the mixer, 290 m3 were recovered CF4 (60%)
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 21: CMS RPC recovery system for C2H2F4 (R134a)
Recovery plant based on distillation process
CMS RPC gas mixture → R134a/SF6/iC4H10 95.2/0.3/4.5
Problem: R134a forms a minimum boiling point azeotrope with iC4H10
Slow heating of liquified azeotrope (red curve) allows to enrich the liquid of R134a and the vapor phase of azeotrope
ELECTRICAL RACK
SEPARATION MODULES
CHILLER
COMPRESSOR
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 22: CMS RPC recovery system for C2H2F4 (R134a)
Thermodynamic simulation done by M. Bruno (PoliTO)
From RPC Exhaust R134a/iC4H10/SF6 = 95.2/4.5/0.3
Pure R134a to storage bottle
Gas exhaust enriched in the azeotrope (R134a/iC4H10 = 65/35)
Liquid R134a descends into the bottom buffer thanks to gravity and vaporizes
Gas phase goes up to the top buffer leading to the distillation
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 23: CMS RPC recovery system for C2H2F4 (R134a)
Distillation units
Compressor module
Storage Tank
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 24: CMS RPC recovery system for C2H2F4 (R134a)
Recovery efficiency of 80% with 5000 ppm iC4H10 in the recuperated R134a (99.5% of gas purity)
Recuperated R134a is reinjected at the RPC mixer in a ratio 50/50 with fresh R134a
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 25: Recovery plants - overview
Positive consequences
Operational budget and GHG emissions reduced
  CF4 recuperation for CMS-CSC
    10% CF4 in gas mixture
    With 65% recuperation efficiency  1400 kg/year CF4 saved (out of 2200 kg/year needed)  -10500 tCO2eq/year (~ -60 kCHF/year, system paid back in 5 years)
  R134a recuperation for CMS-RPC
    95.2% R134a in gas mixture
    With 80% recuperation efficiency (and considering the limit imposed by current leak rate)  12 t/year R134a saved (out of 24 t/year needed)  -18000 tCO2e/year (-130 kCHF/year, system paid back in 3 years)
Difficulties
Gas systems and recuperation plants must be considered as industrial installations
  More than 300 euro-racks that need to be operational 24/7
Additional resources with specific expertise are needed (i.e. chemical engineers, physicists, mechanical engineers)
  Current team profile based on technicians cannot ensure design and proper operation and maintenance following industrial standards
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 26: Conclusions

## Slide 27: Conclusions
Fluorinated gases are responsible for more than 80% of CERN GHG emissions
Gas team started its R&D activities to reduce the GHG emission before F- EU legislation of 2014 was published!
16 recirculation systems & 4 operational recovery systems for GHGs (2 CMS and 2 LHCb) currently operational
These systems implies more control on gas quality  daily gas chromatograph analyses and online monitoring systems (e.g., SWPC and IR)
Modest investment wrt the tCO2e saved and in addition they mitigate difficulties in case of GHG shortage allowing experiment data taking! (as experienced in the past and very likely more in the future)
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team

## Slide 28: Thanks for your kind attention!

## Slide 29: Backup

## Slide 30: Recovery plant VS Abatment system
Towards Sustainable Gas Mixtures For Future Detectors (WG3) – M. C. Arena, on behalf of the Gas Team