| LHC |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Machine Coordinator last week |  |  | J. Wenninger |  |  |
| Machine Coordinator this week |  |  | M. Pojer |  |  |
| Statistics |  |  |  |  |  |
| Availability | %63 |  |  | Stable Beam Ratio | %49 |
| Facility Status |  |  |  |  |  |
| Summary | When the machine is up and beams are available, excellent and smooth performance. The vacuum module in point 2 (cell 6L2) with non-conformity is stable, only a few pressure spikes below interlock level have been recorded. The ALICE experiment is observing steady state background as well as background spikes correlated to vacuum pressures in the LSS. Under investigations with TE-VSC. Unfortunately, the week was interrupted 3 times for important cryo system failures which dominate the downtime. |  |  |  |  |
| Issues | Unfortunately, the week was interrupted 3 times for important cryo system failures which dominate the downtime: - A loose contact on an emergency stop cut the warm and cold compressors in point 8 on Thursday. Downtime 21h. - A SEU on a pressure sensor of the cold compressor that was not properly caught by the new SW protection caused a loss of the cold compressor in point 8 Saturday early morning. Downtime 17h. - A compressed air failure on a cryo valve led to the loss of cryogenic conditions on the triplet in R1 on Monday (11.08) early morning. 10h downtime. |  |  |  |  |
| Plans | Physics, one planned access Friday morning to exchange the FASER experiment emulsions. |  |  |  |  |
| Intervention Request |  |  |  |  |  |
| Yes / No | Duration |  |  | Preferred date/time |  |