## Slide 1: EN-HE Updates
HI-ECN3 WP4 - Coordination meeting #13 – C. Duran Gutierrez, R. Rinaldesi – EN-HE
18-06-2025

## Slide 2: Content
Building 911 Works
Service Building
  3D Model Update
TCC8
  3D Model Update
    CV Mezzanine
  Transport study: from EHN2 to TCC8
  Retention of 2 cranes in TCC8
Ongoing and future assessments
  ECR
  15T crane in Cooling room (B754)

## Slide 3: Building 911 works
Cut the existing end stops and replace them with a steel plate anchored to the concrete wall.  Not possible
Extra coverage ≈ 300 mm
Initial plan to increase crane coverage
Alternative
Crane modification – Removal of end bumper extension
Extra coverage ≈ to be verified on site (around 300mm as well)

## Slide 4: Service Building
3D Model Update
Crane coverage (30T)*
Area covered in the mezzanine
2280 x 3545 mm (provisional)
Pending assessment:
Conflicts with the duct layout
1300 mm interference

## Slide 5: Service Building
Auxiliary hoist (2.5T)*
Extra coverage (compared to the 30T hook)
Height + 500mm*
Lateral approach + 500mm*
Pending assessment:
Conflicts with the duct layout
Auxiliary hoist coverage proposal (1)
To minimize the loss of coverage, the location of the auxiliary hoist will be determined based on the duct layout and the elevation of the first floor.
The auxiliary hoist could potentially be installed:
On an additional structure on the same side as the maintenance walkway (initial proposal)
On the main trolley (with the 30t hoist)
Other custom solutions
We can also assess the possibility of rotating the crane (the maintenance walkway facing b.911)
Pros – More coverage in the mezzanine
Cons – Less coverage in the handling hall
3D Model Update

## Slide 6: Service Building
To minimize the loss of coverage, the location of the auxiliary hoist will be determined based on the duct layout and the elevation of the first floor.
The auxiliary hoist could potentially be installed:
On an additional structure on the same side as the maintenance walkway (initial proposal)
On the main trolley (with the 30t hoist)
Other custom solutions
We can also assess the possibility of rotating the crane (the maintenance walkway facing b.911)
Pros – More coverage in the mezzanine
Cons – Less coverage in the handling hall
1
2
1
2
3D Model Update

## Slide 7: TCC8
3D Models |  | 
Crane Coverage | ST1988294_01 | Provisional (Lateral approach to be confirmed)
Transport volumes - Target | ST1988115_01 | Provisional (target volume clashes with shielding – 42mm)
TCC8 Mezzanine Access | ST1A23812_01 | 3000 x 2000
TCC8 Mezzanine monorail | ST1A45062_01 | Coverage: Length – 4800 mm Height – 3120 mm
3D Model Update

## Slide 8: TCC8
CV Mezzanine
900
200 mm step around the opening

## Slide 9: TCC8
CV Mezzanine
900
900
900
200
Jura side
Jura side
The potential extension of the opening toward the Jura side wall must be carefully evaluated

## Slide 10: TCC8
Spectrometer Magnet (SHiP)
The existing transfer tables may not provide sufficient transport support area for the required length (7250mm)
  Some alternatives under study
  Max height ≤ 620 mm
Space reservation for CV pipes through the shaft
  Could it be less than 400 mm?
3D Model Update

## Slide 11: TCC8
Transport study: from EHN2 to TCC8

## Slide 12: TCC8
It is not advisable to dismantle these doors unless it is very justified and there are no alternative transport routes.
The maximum transport volume is limited by the red door opening and the sector door in TT85:
Max Width = 1500 mm
Max Height = 2032 mm
(verified on site)
Tunnel slope (TT84)  30T maximum.
TT84
1500
TT85 (YDPS01.850) – door 1
1500
2032
2018 – QNL with MAFI KOUBA
Transport study: from EHN2 to TCC8

## Slide 13: TCC8
TT84 Inputs
The yellow door can be dismantled
The concrete blocks can be dismantled
Turning radius will depend on the dimensions and configuration of the equipment to be transported.
Blindage dismountable with chariot à potence
Total Height = 2400 mm
Concrete Blocks 1688 (9B1BE 60)
  1600x800x800
  2500kg
TT83 – TT84 – TT85
3130
2410
TT83 - ST1542986_01
TT85
TT83
TT84
Transport study: from EHN2 to TCC8

## Slide 14: TCC8
TT85 Inputs
The cable trays limit a bit the clearance of the passage in the door area BUT:
  It is not a constraint if enough shielding is dismantled.
A section of the beamline must be dismantled
Turning radius will depend on the dimensions and configuration of the equipment to be transported.
TT84 – TT85
TT85
1800
Transport study: from EHN2 to TCC8

## Slide 15: TCC8
2023 – Chariot Loer + magnet
2018 – QNL with MAFI KOUBA
For heavy or long equipment, a specific transport study shall be carried out to assess the manoeuvring requirements and the feasibility of performing a 180-degree turn.
Concrete blocks will be dismantled as necessary and where feasible.
Transport study: from EHN2 to TCC8

## Slide 16: TCC8
TT85 (YDPZ01.851)
TCC8
Determine the available space in this area that can be designated for handling operations
TCC8 crane
TCC8 Inputs
All transport and handling activities will depend on the new layout planned for TCC8.
If the existing overhead crane is retained in that tunnel area, its hook coverage can be used to assist with transport.
Transport study: from EHN2 to TCC8

## Slide 17: TCC8: Retention of the two overhead cranes
DRAFT
MAIN MOTIVATION
To avoid dismantling the new TCC8 confinement wall each time access to the upstream part of the tunnel is required. Material can be introduced through EHN2
IMPACTS
The new festoon cables will be shorter
The festoon storage area will be moved close to the confinement wall
Loss of crane coverage between cranes in the longitudinal direction (new festoon storage area)
The hook coverage of the existing crane in the transversal direction may be reduced to avoid conflict with the cables in fixed installation
It may be necessary to modify the maintenance walkway of the existing crane (handrails)
New end stops for each crane before reaching the confinement wall
Some modification to the cabling required
Access to the existing crane for maintenance will still be possible via a removable ladder - A corridor shall be kept clear to allow the possibility to attach a removable ladder (position can be modified)
The existing crane has electronic components on-board - Resistance to radiation to be checked
Existing festoon storage area
New festoon storage area with junction box
Control panel
Upstream TCC8
Target Area
≈ 10000
Loss of crane coverage
Confinement wall

## Slide 18: TCC8: Retention of the two overhead cranes
Layouts
Control panel
Upstream TCC8
Target Area
New festoon storage area with junction box
A
≈ 10000
Control panel
Upstream TCC8
Target Area
New festoon storage area with junction box
B
≈ 10000
Control panel
Upstream TCC8
Target Area
New festoon storage area with junction box
C
≈ 10000

## Slide 19: Retention of the two overhead cranes in TCC8
Comments and remarks | Pros | Cons
New confinement wall in TCC8 | Dismantling of the confinement wall between the target area and the upstream section may not be required to transfer material. | No access to the upstream section with the new crane.
Access to the upstream part of TCC8 via EHN2 (if the volume fits the passage ) - 1500(w)x2030(h) in area, and 30t weight (max) | Material transfer from the upstream part of TCC8 to the target area, accessing through EHN2 could be possible. The confinement wall might not be dismantled if the volume fits the door/opening made in the wall. | The volume shall fit in the opening. Loss of crane coverage in the longitudinal direction near the confinement wall due to the space required for the new festoon cable storage area - 10 m estimated, several options to be considered
Festoon cabling for the new crane | Shorter festoons | A dedicated storage area must be designed and built close to the confinement wall and that will imply a considerable loss of crane coverage. Hook coverage of the existing crane in the transverse direction (upstream part) may need to be reduced to prevent interference with fixed cable installations.
Modifications on the cabling of the current crane | Minor works shall be carried out Move the feeding line towards the centre of the tunnel | Minor site works shall be carried out and accounted for prior to the installation of the new crane. – The economical impact must be addressed and responsibilities assigned.
Unlikely event = Major intervention in the crane located in the upstream part of TCC8 (like trolley replacement) | - | Replacing the trolley (for example) of the old crane would require dismantling the new crane and possibly partial dismantling of the SHiP experiment.
Structure (SCE) Pending – feasibility study to determine if both cranes cane operate on the same rails and min. distance between them. |  | It will be more efficient to have two independent rails and corbel support systems, one on each side of the separation wall. This will ensure better load distribution and minimizes the risk of structural interference between the two cranes.
Electrical requirements (EN/EL) |  | Extra power cables Minor works and modifications (re-routing)
IMPORTANT PENDING INPUT – Equipment to be installed nearby the confinement wall and the upstream part of TCC8

## Slide 20: Ongoing and future assessments
ECR - ECN3 Transfer Tables
Document shared with some of you. Any feedbak would be greatly appreciated. (27th June) - https://cernbox.cern.ch/s/OI2EjwA2K7Me4DA
It will be presented at one of the upcoming ICEA meetings (18th July)
B.754
Transport and handling studies. Space reservation
15T Manual overhead crane for the cooling room (R-005)
  A height space reservation of approximately 1000 mm is foreseen for the crane.