## Slide 1
Future Circular Collider
Technical Infrastructure
Comparison criteria for GHC and LCC: Cooling and ventilation
I. Martin Melero, D. Najdrowski, A. Coleman (EN/CV)

## Slide 2
Inigo Martin Melero (EN/CV)
2
0. Definitions
- Primary water  transfers heat load from subcircuits to cooling towers
- Make-up water  compensates losses in cooling towers and is used to produce demineralised water
- Demineralised water  cools sensible equipment like magnets or SR absorbers
- Chilled water  produced at chillers, dissipates heat load from air in AHUs, fancoils
- Industrial water  same quality as primary water, cools equipment like cryogenics
- Clear water  evacuated from infiltrations and drains
- Effluent water  byproduct of blowdown recycling, high salts concentration

## Slide 3
3
0. Definitions
Supply air
Exhaust air
Underground
Surface
Chilled water
Supply
Return
AHUs
Fancoils
Shaft
Cavern
AHUs
Treatment of the air to temperature and humidity conditions
Supply air
Supply air
Exhaust air
Exhaust air
Recycled air
Heating battery
Cold battery
Air filter
Air filter
Air filter
Air filter
Air filter
Fancoils
Recirculation of air through coils to locally adjust temperature conditions
Chilled water
Supply
Return
Supply
Return
Chilled water
Hot air
Cold air
Heat Exchanger
Chilled water supply and return
Blower
Return AHU
Supply AHU
Inigo Martin Melero (CERN/EN/CV)

## Slide 4
1. CV current status
Cooling towers for FCC-ee
Cooling
Ventilation
Demineralised water distribution in Tunnel
Chilled water distribution in Tunnel
Raw water distribution
Effluent water distribution
Are we directly affected by the optics?  NO
Are we affected by systems that are affected by the optics?  YES

## Slide 5
2. Questions by optics
What are the prerequisites you need to perform the comparison?
- At the current design stage, we do not need lattice descriptions / technical and experimental insertions from optics.
- Even though we are not directly affected by optics, we are affected by the heat load changes happening in the other systems interacting with the beam.

## Slide 6
2. Questions by optics
Do you require input from other teams and groups?
YES
Collider, booster magnets  Layout for connection to demineralised water pipes
Heat load to water / air, ∆T… of new magnet design (dipoles, quads, sexts)
How will this affect the power converters + cables to magnets?
Data to be collected shortly via Excel requirements

## Slide 7
2. Questions by optics
Do you require input from other teams and groups?
YES
Vacuum, radiation shielding  Proportion of the 50 MW / beam that now goes to SR absorbers, radiation shielding, photon stoppers and environment
Layout for connection to demineralised water pipes
Heat load to water / air, ∆T… of all these elements
Data to be collected shortly via Excel requirements

## Slide 8
2. Questions by optics
Do you require input from other teams and groups?
YES
Beam Instrumentation  Numbers of BPMs, BLMs in Tunnel, heat evacuated to water / air
Refined conditions like temperature stability
Change of conditions in polarimeter, laser hutch in alcove
Data to be collected shortly via Excel requirements

## Slide 9
2. Questions by optics
Do you require input from other teams and groups?
YES
RF  Layout for connection to demineralised water pipes
Integration in Point H and Point L, refitting of CV services
Heat load to water / air, ∆T… of all cavities, update on Point H and Point L
Updates from other users that might change heat load:
Power converters
Racks from EN-EL
Cryogenics
…
Data to be collected shortly via Excel requirements

## Slide 10
2. Questions by optics
What are the criteria under your scope of study that you consider relevant for the comparison?
The amount of heat load extracted from each equipment
+ heat load  + pumping power, pipes, etc  + cooling tower needs  + cost
The distribution of the heat load
to demineralised water  more cooling capacity
to air  extracted through chilled water via fancoils, - efficient & + cost
Conditions in special areas
stricter conditions  + complexity  + deviations from baseline circuits  + cost

## Slide 11
2. Questions by optics
What output will your team or group provide as a result? How long do you estimate this will take you?
Update of the global thermal load: resizing of chillers, cooling towers, circuits…
Evaluation of the complexity of the systems and refinement of the design (deeper detail)
Some details must be refined anyway for the GHC too
Does the choice of optics have a significant impact on your activities?
- Not directly, but rather on the heat loads / cooling and ventilation requirements of our users, consequence of that choice

## Slide 12
SPARES

## Slide 13
Location | Magnets | Alcoves | SR Absorbers | Detectors | Power converters accelerator | RF underground | Cryogenics* | Underground TOTAL
L-A | 7.1 | 0.9 | 12.5 |  |  |  |  | 
A |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
A-B | 7.1 | 0.9 | 12.5 |  |  |  |  | 
B |  |  |  |  | 1.05 |  |  | 1.05
B-D | 7.1 | 0.9 | 12.5 |  |  |  |  | 
D |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
D-F | 7.1 | 0.9 | 12.5 |  |  |  |  | 
F |  |  |  |  | 1.05 |  |  | 1.05
F-G | 7.1 | 0.9 | 12.5 |  |  |  |  | 
G |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
G-H | 7.1 | 0.9 | 12.5 |  |  |  |  | 
H |  |  |  |  | 1.05 | 45.7 | 2.2 | 50.95
H-J | 7.1 | 0.9 | 12.5 |  |  |  |  | 
J |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
J-L | 7.1 | 0.9 | 12.5 |  |  |  |  | 
L |  |  |  |  | 1.05 | 0.69 | 1.0 | 2.74
*Cryogenic equipment is cooled with Industrial water
Demineralised water loads (MW)
To water
(13.3 + 22.6 + 20.5) / 8 sectors = 7.1 MW
To air
7.1 MW * 5% = 356 kW
Magnets | Cables
352 | 2,500
SR absorbers | Alcoves
250 | 300
TOTAL PER SECTOR
3,402
Thermal loads to air in Arc Sector (kW)

## Slide 14
Exchanges in August, December 2024:
Preferences EN-CV:
Delta P around 3-4 bars, maximum 5 bars
Supply water around 27 C, preferred delta T as high as possible, 20-30 C
Only one circuit is foreseen, for copper.
Info from collider magnets:
Delta T 15-20 C, and delta P around 5-6 bars. Sextupoles challenging to attain 5 bar.
Required supply temperature?
Updated thermal load to water?
Updated thermal load to air?
Info from booster magnets:
Delta T 7-26 C, and delta P around 2-7 bars
Required supply temperature?
Thermal load to water?
Thermal load to air?
Exchange January 2024: Layout
Does this layout still hold? Need to iterate / further define it
Current EN-CV assumption for cost estimate, etc: one manifold every 50 m.
What would the interface magnets/EN-CV be?
The flexibles are already considered as magnets?

## Slide 15
Heat loads (MW) at Cooling Towers, FCC-ee ttbar
Location | Magnets | Alcoves | SR Absorbers | Detectors | Power converters accelerator | RF underground | Cryogenics* | Underground TOTAL
L-A | 7.1 | 0.9 | 12.5 |  |  |  |  | 
A |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
A-B | 7.1 | 0.9 | 12.5 |  |  |  |  | 
B |  |  |  |  | 1.05 |  |  | 1.05
B-D | 7.1 | 0.9 | 12.5 |  |  |  |  | 
D |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
D-F | 7.1 | 0.9 | 12.5 |  |  |  |  | 
F |  |  |  |  | 1.05 |  |  | 1.05
F-G | 7.1 | 0.9 | 12.5 |  |  |  |  | 
G |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
G-H | 7.1 | 0.9 | 12.5 |  |  |  |  | 
H |  |  |  |  | 1.05 | 45.7 | 2.2 | 50.95
H-J | 7.1 | 0.9 | 12.5 |  |  |  |  | 
J |  |  |  | 0.5 | 1.05 |  | 0.01 | 42.56
J-L | 7.1 | 0.9 | 12.5 |  |  |  |  | 
L |  |  |  |  | 1.05 | 0.69 | 1.0 | 2.74
*Cryogenic equipment is cooled with Industrial water
Demineralised water loads
To water
2 beams x 50 MW = 100 MW
100 / 8 sectors = 12.5 MW
Magnets | Cables
352 | 2,500
SR absorbers | Alcoves
250 | 300
TOTAL PER SECTOR
3,402
Thermal loads to air in Arc Sector (kW)
To air
12.5 MW * 2% = 250 kW
Exchanges in November 2022, December 2024:
Delta T = 11 C
Delta P = 2.5 bar
Required supply temperature?
Thermal load to water?
Thermal load to air?

## Slide 16
What does each line mean in terms of kW?
To magnets?
To SR absorbers?
Photon stoppers are included in which category?
Requirements gathering by CV, shortly