## Slide 1: CERN-ABB motorSENSE Project Identifying Energy-Saving Potential through Smart Sensors, Digital Twins and Analytics
28.10.2025
A. Andersen | CERN | EN-CV-CES

## Slide 2: Why Energy Efficiency

## Slide 3: From Global Trends to CERN: The Need for Energy Efficiency
Electric motion drives global sustainability, automation, and mobility
45 % of the world’s electricity is converted by electric motors
Fewer than 25 % are controlled by speed drives
→ Major potential for efficiency gains
CERN’s total electricity use ≈ 1.3 TWh / year
Cooling & Ventilation = 14 % of LHC consumption
+2000 motors operated by EN-CV
Cooling & Ventilation: An Opportunity for Energy Savings at CERN
Global trend: demand for electric motion expected to double by 2040

## Slide 4: CERN-ABB motorSENSE Collaboration

## Slide 5: motorSENSE: a CERN–ABB collaboration born from Big Science Sweden 2020
Duration: January 2022 to December 2023
28.10.2025
Ingo Rühl
EN-CV
Nauman Latif
EN-CV-CES
David Widegren
EN-IM
Han Hubert Dols
IPT-KT
Anders Andersen
EN-CV-CES
Ankush Gulati
Energy Efficiency Lead
ABB Motion Services
Matti Laitinen
Business Research Manager, ABB Motion
Simon Lundberg
Discovery Trainee
ABB Sweden
Kristian Rönnberg
Principal Scientist
Thermal management
Kari Saarinen
Principal Scientist
Data analytics
Dmitry Svechkarenko
Team manager,
Powertrain & Digitalization
Panagiotis Kakosimos
Principal Scientist
Industrial digitalization
CERN team
ABB team
Diogo Monteiro
EN-CV-CL
Nikolina Bunijevac
EN-CV-CL
5

## Slide 6: Collaboration Goals
Goal 1
Creating a roadmap with the aim of achieving a 10-15% overall energy reduction in the cooling and ventilation infrastructure at CERN
Goal 2
Create and validate a system digital twin of the cooling and ventilation infrastructure by enabling online diagnostics and maintenance
Goal 3
Public dissemination of results to share the learnings, best practices to inspire industries and large-scale research facilities around the World to become more sustainable and reliable
28.10.2025

## Slide 7: Approach and Methods

## Slide 8
How would you control your speed in this situation?
1
2
Take your foot off the accelerator and slow down?
Keep your foot hard on the accelerator and control your speed with the brakes?
In cooling systems, controlling flow by throttling valves is like braking while keeping your foot on the accelerator
What is the best approach? – is it obvious?
Speed control
Flow control
It’s all about the right approach to saving energy Choosing the right way to control flow and save energy
Variable Speed Drives control flow by adjusting speed — saving energy instead of wasting it through throttling
Speed control
For a 30% flow reduction:
Throttling → only 11% power saving
Variable Speed Drive → 55% power saving

## Slide 9: Energy Appraisal Finding the balance between efforts and accuracy needed
Method A: Least amount of data
Method C: Large amount of data
Method B: Medium amount of data
Basic motor data
Control method (VSD, DOL, …)
Load estimated or measured by ABB Smart Sensor
Flow data from CERN SCADA system
SCADA flow data
Pump curve data
Effort & Accuracy increase →
+

## Slide 10: Energy Savings Calculations Outcome Method A screening
Top 30 assets → potential savings
> 50 % (VSD) vs approx. 2 % (motor only)
788 assets considered
Assumption:
70% motor loading = 100% flow
The report presents two separate scenarios:
Motor only replacement
Upgrade to Variable Speed Drive (VSD)
Excerpt from Top 30 assets with highest energy savings potential identified.
≈ 60 % of motors operate without speed control
Most are IE1 or IE2 (low efficiency)

## Slide 11: Going Further… Case for a Pumped Network

## Slide 12: Detailed Study of a Pumped Network SF6 to UW65 network – ABB analysis
Flow profile used for estimation
ABB evaluated a representative pumped network in CERN’s Cooling and Ventilation installations to validate the theoretical methods previously presented
Scope
Detailed assessment of a representative pumped cooling network
Network currently operating with combined throttling and bypass regulation
Identification of required modifications for variable-flow operation
Evaluation of energy savings through SynRM + VSD solution
Key outcomes
Confirmed feasibility of variable-flow operation
Estimated 64 % energy reduction (~47 t CO₂ / year)
Return-on-investment under 3 years
Study based on historical flow and operating data (2023)

## Slide 13: Digital Twin Study of the SF6–UW65 Network CERN Controls Analysis
Digital twin reproducing the full hydraulic network – validating and extending ABB’s energy savings assessment.
Scope
Full hydraulic reproduction of the SF6–UW65 network in Flownex digital twin platform
Dynamic simulation using historical operating data and real control parameters
Evaluation of variable-flow operation with CERN’s smart regulation
Key outcomes
Estimated 79 % energy saving, 2 years return-on-investment
Validated feasibility of stable variable-flow operation across all load conditions
Demonstrated the impact of advanced control and regulation strategies on network efficiency
CERN developed and simulated a full digital twin of the same pumped network to validate and extend the ABB analysis using real operating data and advanced control strategies

## Slide 14: Results and Beyond

## Slide 15
motorSENSE Collaboration – Key Conclusions
  17.4% across a fleet of 800 motors based on method A appraisal
  *Based on method A appraisal
  POTENTIAL SAVINGS
  >50%
  on networks suitable for variable-flow operation validated through detailed studies
  POTENTIAL SAVINGS
+
=
+

## Slide 16: Beyond the motorSENSE Collaboration
28.10.2025
2022
2025
10 years
energy efficiency consolidation program
On CERN Cooling and Ventilation installations
Approved in May 2025
Implementation phase to extend efficiency improvements across CERN installations
CERN’s 2022 collaboration with ABB inspired a similar energy-efficiency partnership at GSI in 2025

## Slide 17
Thank you for your attention
Questions?

## Slide 18: ABB Ability Smart Sensor Specifications
More information can be found in ABB Ability™ Digital Powertrain - Condition monitoring of rotating equipment fitted with ABB Ability™ Smart Sensors (EN)

## Slide 19: Monitored Parameters & Advantages
Monitored Motor Health Parameters | Monitored Motor Operating Parameters | Advantages
Overall condition Overall vibration Bearing condition Skin temperature Misalignment | Vibration (radial, tangential, axial) Velocity RMS Acceleration RMS Acceleration peak to peak Speed (rpm) Running time/Operating hours Total number of starts Supply frequency (Hz) Output power (hp/kW) Regreasing count-down Magnetic Field Acoustic signals | Early detection of potential problems minimises unplanned downtime Condition-based maintenance lowers costs Process optimisations reduce operating and energy costs Remote condition monitoring increases personnel safety Operating in explosive atmospheres Easily retrofitted to ABB or third-party equipment

## Slide 20: How Variable Speed Drives Cut Pump Energy Use
Chart: Power vs Flow
| 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
No control | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Throttling/Damper | 0.4134 | 0.5417 | 0.6654 | 0.7748 | 0.8764 | 0.926 | 0.985 | 1
Inlet vane | 0.102 | 0.1793 | 0.265 | 0.3817 | 0.4939 | 0.6451 | 0.8104 | 1
Bypass | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
VSD (Drive) for pumps | 0.1475 | 0.2169 | 0.2839 | 0.3712 | 0.4924 | 0.6102 | 0.779 | 1
Savings
VSDs adjust speed instead of throttling, avoiding energy loss at partial flow
Notes: When pumps operate at partial flow, a lot of energy is lost through throttling or bypassing. Variable Speed Drives adjust the pump speed instead, matching demand and avoiding these losses — that’s where the savings come from.

## Slide 21: Motor Population and Efficiency Baseline Data extracted from ABB motor audit – basis for energy savings calculations
Motor efficiency class distribution
Motor control method breakdown
Most motors are IE1 or IE2
Efficiency ranges for motors
≈ 60 % of motors operate without speed control (DOL, Soft starter, Star-Delta, or 2-speed,)

## Slide 22: CERN Smart Regulation
White paper:
https://inspirehep.net/files/8adf5f2ffa67dd786649f45b274b8125