## Slide 1
Impact of longer flat tops to magnets operation
Leir Heart+ project
Dominique Bodart TE-MSC-NCM 25/08/2025

## Slide 2
The purpose of this presentation is to evaluate the impact of increased flat top duration of the Leir cycle on the main dipoles quadrupoles and sextupoles.
Specifically the total dissipated power for the cooling system capacity and the calculated temperature increase of the magnets is computed.
This will allow to understand if the actual setup in terms of magnets and cooling system is capable of handling the new cycles parameters.
The following magnets are evaluated:
BHN: Main bending magnets
QDN1030, QDN2040, QFN1030, QFN2040, QFN2344: Main quadrupoles
XDN1030, XFN1030: Main sextupoles
They are all groups in family of 4 magnets having identical sets.
Introduction
Fig.1 picture of the present magnet

## Slide 3
For each magnet type the cooling parameters are evaluated:
*To be checked based on local configuration
**Worse value out of the two circuits present in the magnet
Magnets parameters
Table 2. Magnet data
Magnet type | R per coil (mΩ) | R total (mΩ)) | P drop (bar) | Cooling flow (l/min)
Dipole | 3,4 | 6,8 | 12 | 91 *
Quad | 8,2 | 32,8 | 12 | 30 *
Sextupole | 7,8 | 46,8 ** | 12 | 1 *
Table 1. Individual Magnet parameters

## Slide 4
For each magnet type the cooling parameters are evaluated (from E. C.C. Garcia):
Magnets performances
Table 2. Magnet operating R.M.S. current (A)
Table 3. Dissipated power per group of 4 magnets (kW)
Table 4. Temperature increase per magnet type (ºC)

## Slide 5
The calculated temperature increase during the different flat top duration remains at the worse case at 8 ºC for the bending magnet, considering the cooling flow is at 91 l/min which shall be confirmed.
The total dissipated power in the case of the 5 s plateau for the 32 magnets represents an increase of 2,8 times the power w.r.t. the present situation. The increase of cooling demand to the cooling network shall be adressed to EN/CV to ensure operations at 25 ºC input maximum.
Since the operating currents of the main quadrupoles is rather limited with respect to the magnet performances, the temperature increase remain at marginal values of about 1 ºC.
Similar case is for the sextupoles where the temperature increase remains below 1 ºC if we consider a cooling flow of 1 liter per minute which shall be confirmed.
Thermal inspections during new operating sets shall be made to ensure safe and secure operations, considering that the bending magnets have no spare coils.
Conclusions