## Slide 1: Cryogenics for the cooling cell magnets P. Borges de Sousa, T. Koettig, R. van Weelderen
IMCC: Cooling Demonstrator Workshop, 5-7 November 2025, Milan, Italy

## Slide 2: Introduction
As we start to have some preliminary numbers on heat loads for the magnets in the RF Magnetic Field Test Facility (RFMFTF), as well as the required temperature levels, we will try to lay out a few options on how the cryogenic system for the RFMTF could look like, considering that:
There is limited space available
There is no existing He/cryo infrastructure
Please keep in mind that:
The design of the magnet cryostat is at an early stage and being updated, the heat loads are likely to change → this can affect ideal solution
The options for cooling infrastructure discussed here have not been validated w.r.t. installation, cost, etc.. They are shown merely for discussion!
courtesy of M. Statera (link)
Artist’s rendering of an RF Magnet cell

## Slide 3: Changes since Fermilab workshop end of ’24
Heat loads on the previous design were excessively high
Concept of ‘inter-cell cryostat’ developed and reviewed – forces intercepted at cold
Breakdown of heat loads at the different T levels to come soon – update will come soon, and cooling strategy will be updated/refined

## Slide 4: Preliminary heat load estimation for one cell Values from Jan 2024 – to be updated
 | Source | @ Thermal screen T (60/80 K) [W] | @ Cold mass T (20 K) [W]
Static | Conduction via supports | 2 | 6
 | Thermal radiation | 100 | 1
 | Conduction via current leads | 110 | 2
Dynamic | Beam-induced loads | ? | ?
Total steady-state |  | 212 | 9
Transient | Hysteresis losses | N/A | 13
Transient steady-state + transient |  | 212 | 22
 | Source |  | 
Static | Conduction via supports | 2 | 6
 | Thermal radiation | 100 | 1
 | Conduction via current leads | 110 | 2
Dynamic | Beam-induced loads | ? | ?
Total steady-state |  | 212 | 9
Transient | Hysteresis losses | N/A | 13
Transient steady-state + transient |  | 212 | 22
Input courtesy of M. Statera (see link), to be updated w.r.t. latest design (numbers may change esp. regarding conduction)
Assumptions:
Cold mass = 20 K
Thermal shield = 60 K or 80 K (*)
One pair of current leads per cooling cell (**)
Hysteresis losses ~940 kJ/cell → 13 W if charging in 20 h
Powering current 2 kA
(*) Baseline is 60 K, but move to 80 K could simplify cryogenic infrastructure (not only energy consumption but choice of system)
(**) # of CLs may double (2 pairs per cell → 220 W/cell for CLs alone)
Values per cell !
For 30 cells:
6.4-9.7 kW @ 60/80 K
660 W @ 20 K

## Slide 5: Option I – cryocoolers + turbo-Brayton (1/2) Cold mass temperature level @ 20 K
⌀127 mm
For 30 cells:
6.4-9.7 kW @ 60/80 K
660 W @ 20 K
Single-stage GM-type cryocooler such as Cryomech/Bluefors AL630, cooling power 90 W @ 20 K → <10 cryocoolers for the 30-cell cooling channel cold masses
A few considerations:
The cryocooler cold head should remain in < 1 T background magnetic field (moving piston)
The cryocooler motor stalls in magnetic field > 30 mT (“remote”, i.e., decoupled options not available for single-stage GMs)
Option to circulate He in a closed circuit, which extracts heat from the coils to the cryocoolers a few meters away from cryostat (need extra cooling capacity for circulator losses)
Capacity curve AL630
Source: Cryomech AL630
Cold head
Motor
cold source
heat exchanger on GM stage
cold circulator
delivering specified and restoring
magnets
heat exchangers coupled to coils
What about the thermal shield/current lead temp. level?
2-3 m
For = 20 K, needs to be 2-3 K lower

## Slide 6: Example of cooling at 20 K - SHiP
Courtesy L. Baudin (Indico)
Large aperture (4 m x 6 m) superferric magnet
Conductor: MgB2 operating at 18-20 K
Significant energy savings w.r.t. normal conducting option (even when considering cryogenic consumption!)
Installation in area without He infrastructure (ECN3), and relatively low heat load → ideal case for use of use of cryocoolers and a remote supercritical He loop
Three loops using He gas @ ~10 bara and
18-20 K for the cold mass (~ 5 g/s)
70-80 K for the thermal screen (~ 6 g/s)
50-55 K for the current leads (~ 2 g/s)
Advantages:
Cooling infrastructure 15 m away from magnet (high penalty if conduction cooled)
Almost no He inventory
Operation at higher T

## Slide 7: Option I – cryocoolers + turbo-Brayton (1/2) Cold mass temperature level @ 20 K
What does it mean for the cold source for 1 cell:
330 W @ 55 K (TS and CL at 70 K)
22 W @ 17 K (CM at 20 K)
Source: Cryomech AL630 and Al600
Capacity curve AL630
~30 W
@ 17 K ?
2 x F70 compressor
6 m lines
=13.5 kW
2 x F70 compressors
6 m lines
=13.5 kW
440 W
@ 55 K
50 W
@ 17 K
TS: 1 cell per cryocooler
CM: 2 cells per cryocooler
Start with LT version alone until change to TBF
Source: Sumitomo CH-160 D3 (LT)
385 W
@ 55 K
Capacity curve AL600

## Slide 8: Option I – cryocoolers + turbo-Brayton (2/2) Shield / current leads temperature level @ 60/80 K
Source: Air Liquide (link)
Required cooling power at the thermal shield/current level stage is too high for cryocooler use (too many units needed, not energy-efficient, significant tunnel space required, MTBF…)
Alternative: use a turbo-Brayton refrigerator to provide the cooling power to the thermal shield/current lead temperature stage independently from the cold mass:
Fully packaged system with a small footprint (“plug & play”) → can be placed on surface
Designed to be maintenance free
Waste heat can be recovered if needed
Refrigeration & liquefaction up to 70 bar → can accept large along cooling cell string
Cryogenic circulator for LN2, GH2, GN2 and GHe integrated on refrigerator unit
If the temperature level is 80 K rather than 60 K, a LN2 supply dewar at the surface with a transfer line down to TT7 could also be considered → 50 g/s LN2 evaporation → ~4 tons/day!!
For 30 cells:
6.4-9.7 kW @ 60/80 K
660 W @ 20 K
For a cryocooler- or LN2-based solution, choosing a higher T for the thermal shields/current leads (i.e., 80 K) is essential
210 kWel

## Slide 9: Cooling strategy: from a few cells to whole demo
x1 @ 60 K
Cooling cell
CH-160LT
x0.5 @ 20 K
CH-160LT
~ 20 kWel per cell
x14 @ 60 K
14 cooling cells
CH-160LT
x7 @ 20 K
CH-160LT
~ 273 kWel for 14 cells
x1 @ 60 K
14 cooling cells
TBF-175
x5 @ 20 K
CH-160LT
~ 300 kWel for 14 cells
- OR -
Evaluating by power consumption alone, one can progressively implement cooling cells in a modular way using cryocooler-based cooling sources for both TS and CM… if 14-15+ cells, TS can be taken over by a TB machine, and cryocoolers previously used for TS can cool down CMs of future cells

## Slide 10: Option II – Small cryoplant for test facility
Source: Linde Kryotechnik (link)
Both Air Liquide and Linde (and others!) offer compact, small-scale liquefiers or refrigerators with significant cooling power at around 20 K and at 60-80 K
To be investigated if such small refrigerators can provide such asymmetric cooling capacity (~10x more cooling power at 60/80 K than at 20 K)
Using a cryoplant for both temperature levels:
Reduces the number of systems running in parallel
Is more energy-efficient than using cryocoolers
The entire cryoplant can be installed at the surface, only transfer line goes down to TT7
Ancillary services (cooling water, etc.) also remain at surface level
Has possibly a higher cost when compared to cryocooler + turbo-Brayton alternative
Could have synergies with neighboring experiments (larger, shared cryoplant = more efficient, lower cost per W)
For 30 cells:
6.4-9.7 kW @ 60/80 K
660 W @ 20 K

## Slide 11: (Qualitative) comparison of cryo system options
Cryocoolers + turbo-Brayton or LN2
Independent cooling circuit for each temp. level
TB system installed at surface level
Modularity with increasing # cells, can add cryocoolers as cooling channel grows
Cryocoolers + compressors installed underground (needs cooling water + electricity)
High energy consumption (12 kW/cryocooler + TB (?))
Maintenance of cold heads every 15’000 h
Requires trained operators for TB part
He liquefier/refrigerator
(can have) independent cooling circuit for each temp. level
Cold box + ancillary services all at surface level, only transfer line to cooling channel
Most energy-efficient option
Likely higher cost than cryocooler + TB option
High He inventory incl. gas management + storage
Complex maintenance of cryoplant every 8’000 h
Requires trained operators

## Slide 12
Thank you
for your attention!