## Slide 1: sCO2 results DRD8: 2nd Collaboration Meeting WP3
Camila Pedano-Medina
14th of October, 2025

## Slide 2: The critical point
Critical point of CO2 is 73.8 bar and 31.1 ºC
  For any substance, it is the point at which there is no distinction between liquid and vapour phase
Below the critical point:
  An isobaric increase in enthalpy brings us to vapor-liquid equilibrium
  Phase change
Above the critical point,
  Phase change does not occur
  The liquid-like fluid continuously transitions into a vapor-like fluid

## Slide 3: Above the critical point: properties of interest
Density drops from liquid-like density to vapour-like
Heat capacity (Cp) peaks at so-called pseudocritical point (Tm): particularly interesting
Viscosity drops similarly to density
Thermal conductivity peaks and drops
Tm(P)

## Slide 4: Above the critical point
When we approach Tm at a given pressure, the slope of the enthalpy with temperature increases sharply
This means that the enthalpy varies with a small change in temperature
For us, this can mean that we could reach isothermal operation if staying around this region
As we increase pressure, we lose this capability of isothermal operation <> variation of enthalpy with temperature flattens
31.7 ºC

## Slide 5: The sCO2 experimental rig
Operating conditions:
P = 50 - 120 bar
T = 5 – 100 °C
ID = 1 – 3 mm
m = 1 – 11 g/s
Pressure setpoint
Pumping
Temperature setpoint
Return
Test section

## Slide 6: The sCO2 experimental rig
1
2
3
4
Accumulator – pressure control
Pump – flow through the rig
Preheater for desired inlet condition

## Slide 7: Indirect measurement of heat transfer coefficient
Thermocouples
evenly spaced
Inlet fluid temperature PT100
Outlet fluid temperature PT100
Data reduction
1 mm ID pipe

## Slide 8: Results (1 mm pipe)
Operating point: below critical point, subcooled liquid
m = 1.8 g/s
Q = 50 W
L = 1 m
Lheated = 0.9 m
dp = 0.7 bar
72 bar
Tin = 20 °C
Tout = 27 °C

## Slide 9: Results (1 mm pipe)
Data at subcooled liquid conditions shows rather high heat transfer coefficients
Data evaluated at bulk conditions (Gnielinski)
m = 1.8 g/s
Q = 50 W
L = 1 m
Lheated = 0.9 m
dp = 0.7 bar
Heat transfer coefficients along the pipe 12-15E3 W/m2K
Considerable temperature increase in pipe of 7 K

## Slide 10: Results (1 mm pipe)
Moving up in pressure and heading towards Tm
m = 1.8 g/s
Q = 100 W
L = 1 m
Lheated = 0.9 m
dp = 0.8 bar
85 bar
Tin = 31 °C
Tout = 37 °C
Tm(85 bar) = 37.5 °C

## Slide 11: Results (1 mm pipe)
On the left of Tm our HT is similar to that of a subcooled liquid until we really approach the pseudocritical point
Normal Heat Transfer (NHT) regime predictable with D-B type correlation (Gnielinski)
m = 1.8 g/s
Q = 100 W
L = 1 m
Lheated = 0.9 m
dp = 0.9 bar
Heat transfer coefficients along the pipe 15-30E3 W/m2K
Temperature increase along the pipe of 6 K

## Slide 12: Results (1 mm pipe)
Moving to the right and crossing Tm
m = 1.8 g/s
Q = 100 W
L = 1 m
Lheated = 0.9 m
dp = 1.4 bar
85 bar
Tin = 36 °C
Tout = 39 °C
Tm(85 bar) = 37.5 °C

## Slide 13: Results (1 mm pipe)
When moving to the right in temperature and passing by Tm
Heat transfer coefficient peaks and drops after passing by pseudocritical point
m = 1.8 g/s
Q = 100 W
L = 1 m
Lheated = 0.9 m
dp = 1.4 bar
Heat transfer coefficients along the pipe 20-40E3 W/m2K
Temperature increase along the pipe of 3 K

## Slide 14: Results (1 mm pipe) conclusions
Above critical pressure and on the left of the pseudocritical point
Local heat transfer coefficient is enhanced to 20-35E3 W/m2K
Temperature increase along the pipe of 6 K
Still low dp = 0.9 bar
Below critical pressure – subcooled liquid
Local heat transfer coefficients 12-15E3 W/m2K
Temperature increase along the pipe of 7 K
Low dp = 0.7 bar
Above critical pressure and passing by the pseudocritical point
Local heat transfer coefficient 20-40E3 W/m2K
Temperature increase along the pipe of 3 K
Higher dp = 1.4 bar
85 bar, 1 m long
50W
100W
100W

## Slide 15
37.5 ºC
32 ºC

## Slide 16: Applications in microelectronics
In collaboration with DRD7, we will be investigating cold plates for FPGA and other components in the card PCIe40
Current technology uses air cooling (fans won’t be enough soon) and the only commercial option uses water/glycol mixture
Expected power consumption in FPGA = 70 W
No big constraints on temperature
Because of strong dependency of clock speed with temperature, thermal stability should remain within +-0.5K
To achieve such stability in single phase, we must operate near pseudocritical point <> high heat capacity
45x45mm
Transcievers
FPGA

## Slide 17: Applications in microelectronics
Jet impingement cooling enhances heat transfer by directing high-velocity jets onto a surface, creating a stagnation region with developing boundary layers and very high local heat transfer coefficients.
https://indico.cern.ch/event/1583882
Ben Pulver has been designing, testing planned in the coming months
More information in Ben’s talk

## Slide 18: Forecast
Further data acquisition at other system pressures
Further exploration of the isothermal operation concept
Direct comparison of sub-supercritical test conditions in the same rig
Proof of concept in different microelectronics scenarios – synergy with DRD7 (Direct Liquid Cooling)
Jet Impingement

## Slide 19
Thank you