## Slide 1: Occupational Safety – WP6
Jamie Currie HSE-OHS-PE
24/09/2025

## Slide 2: Introduction
Seismic and Structural
Underpressure Cascade
UPS Batteries
Noise Study
Emergency Egress Paths
ODH Risks
General Support
Next Steps

## Slide 3: Seismic and structural regulation
Proposal - Seismic Design Requirement Definition for Equipment and Structures foreseen in TCC2, TCC8, and ECN3
  Study to achieve justification of a satisfactory seismic safety level with no or limited reinforcements
  An advanced geotechnical model and further numerical analyses are needed to define such a design input
  It is also proposed to treat ECN3 and TCC2, as some SHiP detector components and block assemblies in TCC2 present the same problem.
CERN financial contribution be divided equally among the 3 projects (i.e., NA CONS, HI-ECN3 and SHiP), which may participate for 15.1 kCHF each.
Formal approval needed from HI-ECN3 to proceed to formal review and approval process
  Green light received from NA CONS and SHiP

## Slide 4: Underpressure Cascade
Comments delivered by A. Henriques
  Underpressure values during nominal operation are okay and in accordance with previous discussions
  Mention is needed on the underpressure values under the Fire Rated Underpressure System scenario (i.e. emergency mode). These values shall also be estimated and included in the spec so that the project identifies the best way to open the doors in case of evacuation
Comments also delivered on EDMS 3341374

## Slide 5: UPS Batteries
The requirement is to ensure that the under-pressure system is “uninterrupted”, which means that there should be e.g. UPS to bridge the gap between power cut and the diesel generators kicking in
What is the type of UPS system expected to be used?
  Technical specifications sheet
  Type of batteries
  Size (200kVA)?
What is the duration needed of back-up power?
Where will it be placed?
Will there be a battery room?
  If yes, ventilation and fire resistance requirements exist
  Minimum resistance of the compartment = EI 30. Additional requirements may follow, as per the fire safety presentation

## Slide 6: Noise Study
Is acoustic insulation required in or around the CV rooms?
  Input received from EN-CV of all present noise generating equipment
  Layout of building and sensitive areas provided
Preliminary requirements shared
  The CV room should be constructed with concrete walls and fitted with an acoustic door providing a performance of Rw+C = 40–45 dBA.
  Awaiting further response after additional information has been provided
Global noise study to be performed, including SHiP

## Slide 7: Emergency Egress Paths
Egress path - ventilation room
  For the ventilation room in the service building, the only compliant solution is to provide a door (used only during emergencies) towards the electrical room to reach the external stairs
  An egress path greater 40 m will not be accepted as a compliant solution

## Slide 8: ODH Risks
Follow up of the ENTM: Helium cooling system for the HIF (BDF) by Francesco Dragoni / EN-CV
Meeting planned for 25/09/2025 (new date to be confirmed) to discuss all potential leak scenarios and areas of high risk between the service building and target area
Experimental area (SHiP decay volume)
  ODH detectors are today already present in the cavern, next to the krypton cryogenic system
  Initial calculation based on complete release of the entire inventory, relative to the total volume of the cavern, to see the effect on the oxygen level
  No major risk identified – follow up study to be performed
  Consideration is needed for if the helium escapes through the access shaft. Or in the scenario that it bursts or experiences a leak, the direction of release

## Slide 9: General Support
Transport opening + monorail between ventilation rooms - B754
  As a part of the rail must be removed or a gate would be installed then a solution to limit exposure of persons to a fall must be implemented during the material transport process
  Normally personnel would be equipped with fall restraint equipment to ensure they cannot go beyond a certain point when approaching the gate, unlocking it then opening it. Similarly, if the guardrail was to have a removable piece (this may be a cheaper solution than a gate) this procedure would apply
TCC8 and GHN300 evacuation system during dismantling
  The TCC8 and 912 must be equipped with temporary systems for the dismantling period. The sirens must also be extended to GHN300
  The technical aspects such as number and location of sirens depends on the audibility and falls under EN-AA umbrella
  The audibility of the sirens is based on EN 54 which says that siren should be 5 db (10 dB as per French rules) more than the ambient noise
  The manual pushbuttons can be located in the shafts

## Slide 10: Next Steps
Target complex infrastructure workshop
TDR – Occupational Safety
Addressing SHiP Safety Needs in the Context of HI-ECN3
IRP – Shared to HSE-OHS representatives