## Slide 1: ALICE SPD COOLING CRITICAL ISSUES
Rosario Turrisi
2nd SPD Cooling Workshop

## Slide 2: In this talk
Detector’s side cooling system
Performance history
Remarkable events
Flow vs. thermal contact
Recent interventions
Final consideration

## Slide 3: Detector’s (in)side
1sector = 1 cooling line
1 cooling line feeds 6 staves
input: collector box, 6 capillaries 550 mm × 0.5 mm i.d.
output: collector box, 6 pipes ~10 cm long, 1.1 mm i.d.
2 bellows in a row, ¼” tube diameter, 6” and 12” length
bellows
bellows
C side
(liq)
A side
(gas)

## Slide 4: Critical components - 1
Capillaries
  used to enter the coexistence phase
  CuNi, 550 mm long, 0.5 mm i.d.
Cooling pipes
  where the heat transfer happens
  Phynox, 40 μm wall
  round 3 mm pipes squeezed to 0.6 mm inner size
Both sensitive to pollution!

## Slide 5: Critical components - 2
D = 5.6 mm
T = 11.8 mm
X = 0.7 mm (~1 mm in the filtering area)
S = 4 mm
L = ~5000 mm
T
D
X
Filter Swagelok SS-4-VCR-2-60M
Swagelok gland 6LV-4-VCR-3-6MTB7
Pipe: SS 316L 4-6 mm i-o diameter
Swagelok 316 SS VCR Face Seal Fitting, 1/4 in.
Female/Male Nut: SS-4-VCR-1 & SS-4-VCR-1
SEM picture of the filter
S
L
no access

## Slide 9: The picture (as we know it)
Some pollution went into the lines
It had to go through oxysorb/hydrofilter of the plant (1 μm filter was installed after 1 year run)
and/or
It had to go through the first 60 μm inline filter and deposit (and partly go through) the second inline filter
The second clogged filter cannot be replaced (have to disassembly the experiment) and causes:
  less flow
  pressure drop
The liquid heats up to room temperature along the path to the detector (~40 meters) – this was not a problem, if alone
The combination of the last two causes:
  less flow in the single line  worse performance in the sector
  bubbling before the capillaries  local and occasional loss of performance
Most of the effects are reproduced at the test-bench
At least one effect is difficult to reproduce and understand: post-stop/start flow reduction

## Slide 10: Efficiency history
Long stop (you know why…) – minor rerouting of return pipes
First switch on after installation: efficiency = 87%
DSF status (tests pre-installation): efficiency = 100%
Restart after long stop: efficiency = 71%

## Slide 11: Efficiency history
Stable after interventions: efficiency = 83%
Interventions in fall 2009
Last resume after tech stop: efficiency = 64%
extrapolation from last year
assumes constant trend
Start of LS1  <45%

## Slide 12: Critical issues – a list
Pump breakdown
  pressure spikes – correlated?
    we know since 2008
    why only one pump fails? working time? position?
  two-stages pumps?
    need for qualification
  other technologies?
Missing protection against unwanted (and sudden) stops
  chilled water stop
  power failure/glitch
  mixed water stop
Subcooling reliability
  in case of mixed water failure, access inside the magnet could be needed
Leaks
  bad connections & safety valves
Black holes
  where the pollution came from
  cause(s) of performance drop at (technical) stops

## Slide 13
Flow instability during 2010
-11% of flow in 2 months
To vacuum the bad loops before the restart can help to recover the flow
From:
C. Bortolin
1st Cooling Workshop
Jan. 12 2011

## Slide 14: Situation after 2010 WS
Cleaning of 4 sectors’ lines (sector nrs. 3,5,6,7) counter-flow
  1h flow w/nitrogen + 24h C6F14 flow + nitrogen flow to remove liquid leftover
Sector # | BEFORE | NOW
0 | 1.85 | 1.98
1 | 1.95 | 2.00
2 | 2.05 | 1.99
3 | 1.16 | 1.79
4 | 1.4 | 1.56
5 | 1.1 | 1.28
6 | 0.85 | 0.9
7 | 0.68 | 0.62
8 | 1.83 | 2.01
9 | 0.49 | 1.93
Notes:
values ~2 have been tuned by hand , could be more
clear improvement in sector 3, 4, 5
situation stable in # 6,7
line of sector #9 is behaving normally, issue of flow between PP4 and PP1 (as we know)
SECTOR #3: ALL HS ON !!! (absolute première)
93 HS on, missing 2 from sector #9 (by-passed)
By-passed by
a dummy sector
w/plastic pipes

## Slide 15: Flow/power correlation
Slowly decreasing trend of flow
The flow doesn’t tell the whole story – stable # of modules must depend on local thermodynamical conditions (not monitored)
The flow itself depends on something not understood
  start/stop’s result often in flow reduction as after last TS
total power
total flow
number of hs ready
Aug 2010
Aug 2011
Sector | Flow (g/s) |  | Trend (g/s) | Δp PP4 (bara) | Flow(g/s)
 | Pliq 6.1 bara |  |  |  | P liq. 6.5 bara
 | Before TS | After TS |  |  | 
0 | 1.98 | 2.01* | +0.03 | +0.96 | 2.09
1 | 1.94 | 1.67 | -0.27 | +0.43 | 1.82
2 | 1.93 | 1.90 | -0.03 | +0.60 | 2.02
3 | 1.24 | 1.05 | -0.19 | 0 | 1.12
4 | 1.32 | 1.15 | -0.17 | 0 | 1.24
5 | 1 | 0.93 | -0.07 | 0 | 1
6 | 0.83 | 0.78 | -0.05 | 0 | 0.84
7 | 0.37 | 0.17 | -0.20 | 0 | 0.19
8 | 1.48 | 1.35 | -0.13 | 0 | 1.45
9 | 0.28 | 0.23 | -0.05 | 0 | 0.26
TOT | 12.37 | 11.24 | -1.13 |  | 12.03
-9.1%
-2.7%
after 11/2011 TS

## Slide 16: Thermal contact
Could thermal contact be another issue?
Performed with AOS 52029 thermal grease
  real K measured (slightly less than promised)
  mechanical stress tested
Long term performance?
Thermal/mechanical stress?
It is a minor issue (by now): good sectors
do not show a worse performance

## Slide 17: Recent interventions
Ultrasounds cleaning
  piezoceramics brought in front of the filters
  cycles of 2 h (alternate 2 h of mechanical bumping with stainless steel wire)
  two sectors treated
  no evidence of effect
Regularly
  counterflow flushing
    last time: 4 days on same sector, gain ~10% of flow
  filters replacement
    SEM analysis on both faces of the filters show no pollution

## Slide 18: Current performance
Flow: 11.6 g/s (nominal: 18 g/s)
Modules ‘’on’’: 75/120, i.e. 62.5 % (off not because of cooling: 3)
Power consumption: 850 W (nominal: 1500 W)
Inlet pressure: 6.3 bara (with a jump to 6.5)
  was ~4 in 2008, 4.5 end of 2009, 5.5 end of 2010…
  maximum we dare to go: 7 bara at the plant
Sectors 7, 9 off – 6,5 in very bad shape

## Slide 19: What’s next
Get rid of those filters ‘’the hard way’’…
  laser
  drill
Keep testing the strategy (‘’in case everything else fails’’…) on the test bench
Thanks for the attention!
see Claudio’s talk
see Andrea’s talk

## Slide 20: Backups

## Slide 22: Layout of the circuit
(2) Target point
The pipe is in yellow
The access point (1) is ~4.5 m away from the target point (2).
The pipe is not fixed but laying in the aluminium box (below the yellow pipe in the exploded view)
The pipe will be filled with liquid (C6F14) or flushed at low pressure (0.5 bar) with the same liquid
(1) Access point

## Slide 23: ‘Ice age’ test
We installed an ‘intercooler’ on the freon line in PP4 (close to SPD)
  8 m of plastic pipe in a bucket filled with ice (many thanks to CERN Restaurant #1!)
  freon reached ~8 °C in PP4
  Test done on 2 sectors (#6 and #5)
Observed:
  increase of flow in one case (∼50%)
  clear improvement of performance
  in both cases 6/7 half-staves recovered !

## Slide 24: Measurement of flow
Very low flow rate in sectors 7 and 9;
Reynold’s number vs. pressure
2300

## Slide 25
Pipes New routing (Symmetric inlet)
View from A side (front)
side ‘I’
side ‘O’
5HX
10 New pipes
~ 10 ˚C
~ 20 ˚C
~ 20 ˚C
~ 10 ˚C
~ 10 ˚C
5 pipes
5 pipes
Flow ~16 g/s
5HX

## Slide 26
Size: 16x26 meters
Weight: 10,000 tons
SPD Cooling station
~50 m
SPD
~8 m
Ri = 39.3mm
Ro= 73.6mm
L = 282mm
Silicon Pixel Detector
SPD
SIDE C
SIDE A

## Slide 27: SPD structure
SPD
Sector
Half-barrel
Half-stave
Ladder
5 sectors
12 half-staves
2 half-barrels
1 sensor
5 read-out chip
2 bump bonded ladders
1 MCM
1 multilayer bus
Total:120 half-staves
1200 ASIC
9.83 × 106 channels
half-stave= basic working unit

## Slide 28: Principle of operation
Joule-Thomson cycle
  sudden expansion + evaporation at constant enthalpy
Fluid C4F10: dielectric, chemically stable, non-toxic, convenient eos
  Nominal evaporation: 1.9 bar, 15°C
PP=patch panels
  PP3: close to the detector, not (immediately) accessible, PP4: ~6 m upstream SPD
~40m liquid pipes 6/4 mm
~35m gas pipes 12/10-10/8 mm
heaters
PP4
PP1
PP3
p, T
Filters (60μm)
liquid pump
capillaries
condenser
compressor
cooling tube
enthalpy
pressure
two ‘knobs’:
liquid-side pressure flow
gas-side pressure temperature

## Slide 29: Test in the lab
very stable against changes in parameters settings (1-2 sectors at a time)
100% efficiency
  tested one half barrel at a time
  full power to the detector (~150 W/sector)
For ~ 3 years the system has been tested in the DSF at CERN
In the lab, filters where missing (60 μm in line and the final 1 μm filter on the plant)

## Slide 30: Looking for the ‘’unsub’’
Pressure increase line by line
  Check if performance can be recovered by increasing the flow
  The flow is enhanced by the pressure increase
Lines swapping
  Could be something related to the lines’ path/conditions
  Some dependence is found – replaced lines with symmetric and shorter path
Lines insulation
  Heating up the fluid can cause early bubbling
  Impossible to insulate the lines – too much surface w.r.t. the volume
SEM analysis of ‘first-stage’ filters
  Clogging material in the lines?
  Keystone test…see later
‘’Ice age’’ test
  Further subcooling to avoid early evaporation: 8 m of pipe in a bucket filled with ice (thanks Restaurant #1) in PP4 (~6 m before the detector)
  Two lines tested, flow increased, 6-7 hs/sector recovered, in one line +50% of flow

## Slide 31: Pressure correlations
Sector #0 (‘good’)
Observed behaviors:
“Good” sectors have a higher pressure drop
“Bad” sectors are more “sensitive” to pressure
changes …
bad guys
Principle: look at the correlation (slope) between the pressure set at the plant and the pressure close to the detector
Test done in 2009
PLANT
SPD
liquid
gas
P
P

## Slide 32: SEM analysis
Analysis of a filter taken from PP4, in place for 1 year approx.
Results and conclusions: “In the used filters several exogenous fragments were located clogging the filter. There were several fragments containing different composition elements. In addition to elements from the Stainless steel, the following traces of elements were found: O, Al, K, C, Sn, Cu, P, Ca, Cu, Na, Cl and Zn.”
Possible origin of the fragments:
pumps (graphite)
hydrofilter (aluminium oxide)
weldings (TIG weldings remnants)
NB lines: electrocleaned s.s. pipes (Sandvik), flushed after installation with liquid freon
clean filter
20 μm

## Slide 33: ‘’Upgrades’’
Installation of a 1 μm at the plant (in 2008)
Installation of new liquid-side pipes
  dedicated path of new lines, more straight (less elbows), shorter
  inox SS316L, 6/4 o/i diameter (same as before)
  no insulation (useless)
Additional heat exchangers to cool the fluid close to the detector
  10 HX’s (one per line), redundat exchange factor (more than 5 times)
  use leakless system with water cooled down at 7.5 °C
Flushing each line counter-flow wise
  drain particles clogging the filters outside the line
  redundant protection against overpressure: 2 safety valves (mechanical) + pressure switch (electronic)
  2 filters, stainless steel, 1 μm grid, on the “washing machine”
  1 to 4 days washing cycle per each sector