## Slide 1: SPD Cooling workshop: PLC item details

## Slide 2
ups upgrade: 10-12' after trigger 24V - what to do in 10 minutes
Present situation:
In case of “normal power” interruption, the plant will go in STOP mode.
Plant will stay in Stop mode after re-powering, waiting for expert acknowledgement.

## Slide 3
ups upgrade: 10-12' after trigger 24V - what to do in 10 minutes
Proposal (1):
Keep running during 2 seconds, then switch to RECOVER mode.
-This approach permit to keep the system stable for m-interruption.
In case of longer power cut (>2”), recovering of the maximum amount of C4F10 in the tank
If the power failure < than the UPS capacity, keep the system in RECOVER mode, waiting for expert acknowledgement.
If the power failure > than the UPS capacity, Plant will go to STOP mode when UPS is down, Pant will be in Stop mode after re-powering, waiting for expert acknowledgement.
Alarm detection:
Control of the “normal power” status in SPD cooling cabinet
Benefits:
Easy to implement, software and cabling modification restricted to the cooling plant electrical cabinet
Concern:
This alarm is not triggered directly from the “Detector” power source status. We may have the following dysfonction:
1/ Alarm triggered from a real local power failure in the cooling plant cabinet, but SPD detector is still powered (unwanted interruption)
2/ “normal power” is alive into the cooling plant cabinet, but SPD detector is not anymore powered (unprotected)

## Slide 4
ups upgrade: 10-12' after trigger 24V - what to do in 10 minutes
Proposal (2):
1/ Keep running during the all UPS capacity, then switch to STOP mode.
-This approach permit to keep the system stable for long interruption.
If the power failure > than the UPS capacity, Plant will go to STOP mode when UPS is down, Pant will be in Stop mode after re-powering, waiting for expert acknowledgement.
Alarm detection:
none
Benefits:
Very easy to implement, software modification only.
Exclude more interruption of the cooling in the long terme.
Avoid the 2 “false alarms” described in proposal 01.
Concern:
The cooling will not stop automatically if the detector is not powered (like it is today).
An hardware interlock between SPD detector & SPD cooling is probably required.

## Slide 5
pressure increase - modifications needed to work at 7 bara
Present situation:
Liquid outlet pressure Warning: 6.8 bara
Liquid outlet pressure Alarme: 7.0 bara
Loop outlet pressure Warning: 6.7 bara
Pump pressure switch: ??.
Proposal :
(rem. That the lipuid pump can run up to 9 bar (source: jose)
PLC code modification + setting:
Liquid outlet pressure Warning: 7.3 bara
Liquid outlet pressure Alarme: 7.5 bara
Loop outlet pressure Warning: 7.2 bara
Pump pressure switch: 7.5
PID regulation need to be optimized
Plant modification:
Re-calibration of the 3 “common” reliefs valves to 10 bara.
Re-installation of the 10 loop’s reliefs valves to 7.5 or 8 bara
Planning: around 1 day for hardware + 1 day for commissioning
Benefits:
Higher outlet pressure (  )
Concern:
Reliability of the liquid pumps is inversely proportional to the delta-p..
Regulation problems may appeared, we experienced that when the plant was modified to 6 bara, we have no guaranty to find “software solution”.
Detector safety: more pressure, more risks.. as to be carrefully evaluate by SPD expert..

## Slide 6
chilled water failure procedure - 10-15' to detect temperature increase and react - how?
Present situation:
In case of chilled water failure, the plant will go in STOP mode.
Plant will stay in Stop mode after re-powering, waiting for expert acknowledgement.
Detection of chilled water failure is triggered when:
the tank pressure > 2.8 bara, OR
Chilled water inlet temperature > 21.0 celcius
REM: Tank pressure setpoint = 2.2bara
Tank pressure warning = 2.4 bara
Tank pressure alarm = 2.8 bara
Proposal (01):
Do nothing.. Cooling plant is properly protected..
Benefits:
Easy to implement
Minimize cooling interruption
Concern:
??

## Slide 7
chilled water failure procedure - 10-15' to detect temperature increase and react - how?
Proposal (02):
Implement an intermediate level on the tank pressure value to trig an alarm then switch the plant to Stand-by mode, starting recovering the fluid.
Benefits:
To be defined..
Concern:
More cooling interruption.

## Slide 8
pump rump up - alarm triggered during last technical stop(overpressure in liquid manifold)
Present situation:
Regulation problems appeared with high pump outlet pressure and sometime cavitations problems (gas/bubbles on the pump inlet)
Proposal (01):
Fine tuning of the PID parameters and longer ramp on the pressure setpoint.
Benefits:
Easy to implement (1 day)
Concern:
Success is not guaranty 100%.

## Slide 9
pump rump up - alarm triggered during last technical stop(overpressure in liquid manifold)
Proposal (02):
Upgrade the plant with a pressure damper on the liquid side.
(then apply proposal 01)
Benefits:
Improve protection of the liquid pump
Much better chance of success.
Concern:
Need mechanical modification.