## Slide 1: MARCO UNICOS based control system CERN 10.09.2012
Lukasz Zwalinski – PH/DT Maciej Ostrega – PH/DT

## Slide 2
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Presentation overview
I/O requirements & system architecture & hardware
Control rack assembly
Software principals
Software development
User interface
Access control
Supervision layout
SCADA interface
Supervision tools
Touch screen
Online pressure enthalpy diagram

## Slide 3
I/O number & system architecture & hardware
Component | Type | Piece
S7-300 CPU 315-2 PN/DP | 6ES7315-2EH14-0AB0 | 1
S7, MICRO MEMORY CARD | 6ES7953-8LL20-0AA0 | 1
S7-300, 8AI, RES. 9/12/14 | 6ES7331-7KF02-0AB0 | 5
S7-300, 8AO, U/I, 11/12 BITS | 6ES7332-5HF00-0AB0 | 1
S7-300, 8AI ,2/3/4 Wire Resist Res9/12/14 | 6ES7331-7PF01-0AB0 | 1
S7-300, 32DI, 24 V DC, 1 X 40 PIN | 6ES7321-1BL00-0AA0 | 1
S7-300, 32DO, 24V DC, 0.5A | 6ES7322-1BL00-0AA0 | 1
SIMATIC 8" TOUCH TFT MULTI PANEL | 6AV6643-0CB01-1AX1 | 1
I/O Type | Number
DI | 32
DO | 32
AI | 34
AO | 8
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Control system architecture
Selected hardware conforming CERN standard
I/O requirements

## Slide 4
Rack assembly – completed thanks to MPI
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Control rack waiting to be placed into MARCO frame.

## Slide 5
UNICOS CPC 6 - framework
UNICOS‐CPC 6 framework
UNified Industrial COntrol System
Continuous Process Control
UNICOS framework supports 3 control system layers:
supervision (SCADA: WinCC-OA)
control (PLC: Siemens S7 and Schneider)
field layer
The package of programming tools includes:
baseline library (with modular PID algorithm)
code generator
skeleton templates and example of objects list
Object definitions provided by UNICOS are split into:
I/O Objects (Digital Input, Digital Output, Analog Input)
Field Objects (OnOff, Analog, AnaDig, Controller, etc.)
Process Control Objects (PCO)
Offers homogenous user interface
More information can be fond at CERN EN/ICE web pages:
http://j2eeps.cern.ch/wikis/display/EN/UNICOS-CPC+Documentation
https://edms.cern.ch/file/1228441/1.3.1/UCPC6_Operator_Training.pdf
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 6
On/Off object example
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 7
On/Off object example
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Name | Type | Meaning
StsReg01 | SHORTINT16 | Status register 1
StsReg02 | SHORTINT16 | Status register 2
SCADA inputs:
Name | Type | Meaning
ManReg01 | SHORTINT16 | Manual register 1
SCADA Outputs:
Name | Type | Meaning | Description | BitPosition
ManReg01 | SHORTINT16 | Manual Register 1 | Manual Register 1 | -
MAuMoR | BIT1 | Manual Auto Mode Request | Manual Auto Mode Request: The operator requests the Auto Mode. | 0
MMMoR | BIT1 | Manual Manual Mode Request | Manual Manual Mode Request: The operator requests the Manual Mode | 1
MFoMoR | BIT1 | Manual Forced Mode Request | Manual Forced Mode Request: The operator requests the Forced Mode. | 2
MSoftLDR | BIT1 | Manual Software Local Mode | The operator requests the Software Local Mode | 3
MOnR | BIT1 | Manual On Request | Manual On Request: The operator requests the On/Open position | 4
MOffR | BIT1 | Manual Off Request | Manual Off Request: The operator requests the Off/Close position | 5
MEnRstartR | BIT1 | Manual Enable Restart Request | Manual Enable Restart Request: The Operator requests a Manual Restart after Full Stop | 9
MAlAckR | BIT1 | Manual Alarm Acknowledgement Request | Manual Alarm Acknowledgement Request: The operator requests Interlocks or Alarms acknowledgement | 15

## Slide 8
On/Off object example
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Name | Type | Meaning
StsReg01 | SHORTINT16 | Status register 1
StsReg02 | SHORTINT16 | Status register 2
SCADA inputs:
StsReg01 | SHORTINT16 | Status Register 1 | Status Register 1 | -
OnSt | BIT1 | On Status | On/Open Status | 0
OffSt | BIT1 | Off Status | Off/Closed Status | 1
AuMoSt | BIT1 | Auto Mode Status | Current status of the Auto Mode | 2
MMoSt | BIT1 | Manual Mode Status | Current status of the Manual Mode | 3
FoMoSt | BIT1 | Forced Mode Status | Current status of the Forced Mode. | 4
LDSt | BIT1 | Local Drive Status | Current status of the Local Mode. The object is driven locally. | 5
IOErrorW | BIT1 | Input/Output Error Warning | Current status of the IOError | 6
IOSimuW | BIT1 | Input/Output Simulated Warning | Current status of the IOSimu | 7
AuMRW | BIT1 | Auto Manual Request Warning Status. | Auto and manual requests discrepancy when Manual/Forced mode active. | 8
PosW | BIT1 | Position Warning | There is discrepancy between the order status and the position status according to Time Delay and Dead-band. | 9
StartISt | BIT1 | Start Interlock Status | Current status of the Start Interlock | 10
TStopISt | BIT1 | Temporary Stop Interlock Status | Current status of the Temporary Stop Interlock | 11
AlUnAck | BIT1 | Alarm UnAcknowledged | Alarm UnAcknowledged: The alarm or at least one of the alarms associated to the object is not acknowledged | 12
AuIhFoMoSt | BIT1 | Auto Inhibit Forced Mode Status | Auto Inhibit Forced Mode status: Current status of the Auto Inhibit forced mode. | 13
AlSt | BIT1 | Alarm Status | Alarm Status | 14
AuIhMMoSt | BIT1 | Auto Inhibit Manual Mode Status | Auto Inhibit Manual Mode Status | 15
StsReg02 | SHORTINT16 | Status Register 2 | Status Register 2 | -
OutOnOVSt | BIT1 | Output On Order Value Status | Output On Order Value Status | 0
AuOnRSt | BIT1 | Auto On Request Status | Auto On/Open Request Status | 1
MOnRSt | BIT1 | Manual On Request Status | Manual On/Open Request Status | 2
AuOffRSt | BIT1 | Auto Off Request Status | Auto Off/Close request status | 3
MOffRSt | BIT1 | Manual Off Request Status | Manual Off/Close request status | 4
HOnRSt | BIT1 | Hardware On Request Status | Hardware On/Open request | 5
HOffRSt | BIT1 | Hardware Off Request Status | Hardware Off/Close request status | 6
FuStopISt | BIT1 | Full Stop Interlock Status | Full Stop Interlock Status | 10
EnRstartSt | BIT1 | Enable Restart Status | Manual Restart after full stop status | 11
SoftLDSt | BIT1 | Software Local Mode Status | Current status of the Software Local Mode. | 12
 |  |  | When true, the alarm or any of the device dependant alarm objects have | 
AlBW | BIT1 | Alarm Blocked Warning | been blocked by the operator | 13
OutOffOVSt | BIT1 | Output Off Order Value Status | Output Off Order Value Status | 14

## Slide 9
UNICOS project development
Local SCADA Server
Logic Generator
Instance Generator
Specification XML
Siemens PLC
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
2 software production iterations completed.

## Slide 10
Supervision layout
Header
  fixed area (toolbar)
Process area
  Synoptic
Footer
  Contextual area
  Historic
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 11
WinCC-OA access
Right click on the Current user name or click on the key
Click Login as
Enter an authorized NICE user / password
Main Access Groups:
Monitor
Operator
Expert
Admin
Only NICE authorized users (defined previously)
are allowed to be log in the WinCC-OA.
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 12
Supervision layout: Process Area
Static info
Text
Drawings
Animated Widgets
Sensors
Actuators
Controller
Process unit
Alarms
Widget interactions
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Sensor
Actuator

## Slide 13
PLC actions representation on WinCC-OA panels
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
MARCO plant

## Slide 14
PLC actions representation on WinCC-OA panels
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
MARCO alarm panel

## Slide 15
PLC actions representation on WinCC-OA panels
Electrical diagnostic
Stepper
Accumulator Auto SP calculation
Accumulator limiters
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 16
Supervision tools
Event list
Alarm list
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 17
Supervision tools
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
Device Tree overview

## Slide 18
Recipes and user defined trends
Recipe component
User defined trends
Recipe: Massive parameterization (optional)
Alarm thresholds
Set Points
PID parameters
Trends:
Trend tree
Individual trends via object face plate
Dynamic trends
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 19
PCO Alarms with SMS or email notification
Digital and Analog Alarms
Types:
Full Stop interlock (FS): Stop the unit/actuator (all dependent units/actuators are set to their fail-safe position) and wait manual acknowledgement before restarting.
Temporary Stop Interlock (TS): Stop the unit/actuator (all dependent units/actuators are set to their fail-safe position) and restart automatically when the interlock disappears.
Start Interlock (SI): Prevent the unit from starting (all dependent units/actuators stay in their fail-safe position).
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 20
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
SIMATIC MP 277 8" TOUCH MULTI PANEL
ACCESS CONTROL PANEL
NAVIGATION BUTTON

## Slide 21
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
ON/OFF WIDGET
ON/OFF FACEPLATE

## Slide 22
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
ANALOG INPUT
WIDGET
ANALOG INPUT
FACEPLATE

## Slide 23
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
PID CONTROLLER
WIDGET
PID CONTROLLER
FACEPLATE

## Slide 24
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
ANALOG
WIDGET
ANALOG
FACEPLATE

## Slide 25
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
ANADO
WIDGET
FULL STOP
INTERLOCK
ANADO
FACEPLATE

## Slide 26
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
ANALOG ALARM
FACEPLATE
ALARM ACKNOWLEDGE BUTTON

## Slide 27
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
DIGITAL ALARM
FACEPLATE
ALARM
BLOCKED

## Slide 28
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
PCO FACEPLATE
PCO
WIDGET
PCO ALARMS

## Slide 29
MARCO touch panel in UNICOS
MARCO 10th September 2012 L.Zwalinski, M.Ostrega

## Slide 30
Online p-H diagram
MARCO 10th September 2012 L.Zwalinski, M.Ostrega
* Still to be implemented in MARCO WinCC-OA applications

## Slide 31
Thank You for Your attention.
UNICOS framework - more details can be found:
http://j2eeps.cern.ch/wikis/display/EN/UNICOS-CPC+Documentation
MARCO 10th September 2012 L.Zwalinski, M.Ostrega