## Slide 1: Current Limitations and Plans for CRYO System (arc and insertions) 3rd HL-LHC Parameter and Lay-out Committee
Rob van Weelderen,
Cryogenic Group, Technology Department, CERN
based on 2nd HL-LHC -- LARP meeting in Frascati (Nov 2012) of Laurent Tavian
with the contribution of K. Brodzinski, G. Ferlin, U. Wagner

## Slide 2: Content
Overall HL-LHC layout
Local and global cryo-limitation in Sectors
Specific Inner Triplet cryo-limitations
Cryogenic layout proposals at:
    Point 1 and Point 5
    Point 4
    Point 7
Specific studies and tests
Schedule and conclusion

## Slide 3: Overall HL-LHC layout
HL-LHC cryo-upgrade:
  2 new cryoplants at P1 and P5 for high luminosity insertions
  1 new cryoplant at P4 for SRF cryomodules
  New cooling circuits at P7 for SC links and deported current feed boxes
  Cryogenic design support for cryo-collimators and 11 T dipoles at P3 and P7

## Slide 4: Sector heat loads: local limitation (valves, HX, piping,…)
Synchrotron radiation 
Image current 
Beam gas scattering 
Resistive heating 

## Slide 5: Sector heat loads: global limitation
Load transfer from 1.9 K to 4.6-20 K refrigeration
Installed
(as specified)
~1 W/m per aperture available for e-cloud
 ~20 % lower than local
limitation (OK !)

## Slide 6: Specific present IT cryo-limitations
Point (status 25.03.2010) | Present Cryogenic power available for secondaries (W) | After LS1 Cryogenic power available for secondaries (W)
L1 | 147 | 270
R1 | 270 | 270
L2 | 147 | 270
R2 | 270 | 270
L5 | 270 | 270
R5 | 147 | 270
L8 | 147 | 270
R8 | 270 | 270
Present Inner Triplets have limitations for extraction of secondaries due to:
Collapsed and repaired, with lower capacity, HeII two-phase heat exchanger (will not be consolidated)
Erroneous mounting of passive heating strips for excess liquid evaporation (will be consolidated in LS1)

## Slide 7: Main components at Point 1 and 5
?: For Q5, Q6 and probable Q7+ ? 1.9 K or 4.5 K operation
will influence the cryo QRL interface significantly
(1.9 K needs 2 jumpers with present QRL design hardware)
Inner triplet
Matching section
Matching section
Continuous
cryostat
Continuous
cryostat
?
?
?
?
(& quench buffers)
Ground level
Shaft
Cavern

## Slide 8: P1 & P5 layout 1: Matching section cooled with sector cryoplants
P1 or P5
S81 or S45
S12 or S56
Q5, Q6 and probable Q7+ ? 1.9 K or 4.5 operation
Note: Cryo for Sector- and LSS-powering are combined except for IT & D1

## Slide 9: P1 & P5 layout 2: Matching section cooled with inner triplet cryoplants
P1 or P5
S81 or S45
S12 or S56
Q5, Q6 and probable Q7+ ? 1.9 K or 4.5 operation
Note: Cryo for Sector- and LSS-powering are as well separated
(links and DFBA / DFBX leads re-arrangement)

## Slide 10: LSS specific magnet cryo-layout issues
Stand-alone magnets 1.9 K cooling QRL interface requires more space than 4.5 K cooling in with present QRL / jumpers / Service modules design (either 2 service modules, twin-DFBX-like module, both with QRL extensions)
D2-Crab cavities-Q4 layout would need 3 jumpers if Crab cavities cryostat are kept independent (cold / warm transition) from neighbouring magnets
IT cooling arrangement under study with TE-MSC-LMF, TE-MSC-CMI (# of jumpers, D1 and/or CP conduction cooled, link cooling, phase-separator placing, piping sizing, beam-screen)
In the light of the above, adapting the existing QRL to the HL-LHC LSS needs might be possible but looks increasingly difficult

## Slide 11: Comparison of layouts at P1 and P5
 | Advantage | Drawback
Layout 1: MS with sector | Corresponds to the CtC baseline (minor modification on the existing QRL, i.e. only new jumper extensions foreseen)… | …but reuse of existing QRL if the new MS layout largely differ from the existing one (operating temperature and/or new equipment (D2, CC, Q4, Q5, Q6? Q7+?…)) could be also expensive and space consuming… …and maybe not feasible!
Layout 2: MS wit IT | Optimisation of the distribution and space with respect to the HL-LHC need. Allow the upgrade of “A” boxes during LS2 Complete sectorization of MS + IT allowing mechanical intervention without warm-up of the two adjacent sectors (but interconnection, if any, must be designed accordingly) | Increase of the CtC (~1 km of compound transfer line with ~20 service modules)  additional cost (8-10 MCHF tbc)
Layout 2 as future baseline? Decision needed

## Slide 12: Interconnection for partial redundancy
Present redundancy baseline w/o interconnection (IB) in between cryoplants !
“Partial” redundancy: - cold standby during technical and Xmas stops
- low beam-intensity operation in case of major breakdown on the new cryoplant (full nominal redundancy not possible) - what about redundancy with detector cryogenics ?
Cost increase

## Slide 13: Interconnection box (IB)
Up to 10 cryogenic valves to be integrated in the tunnel (space ?)
 Volume in between valves used as controlled volume for safe cryo-consignation
 Valve DNs depend on the level of needed redundancy

## Slide 14: Space requirement in caverns and shafts
Shaft requirement In addition to the 3 SC links:
- 1 compound cryoline (~DN500)
- 3 warm recovery lines (~DN100-150)
Cavern requirement:
- 1 cold compressor box

## Slide 15: Minimum CCB requirement in cavern
Depending of the
total cooling capacity and
operating temperature
Single CC train
Double CC train
Best for cavern integration
Global or distributed ?
(500 W max size for distributed HX !)
500 W HX

## Slide 16: Number of cold compressor trains
LHC sector
Present HL-LHC
Requirement (tbc)

## Slide 17: Minimum size of cold compressor box (CCB)
~6 m
~1.6 m
~5.5 m
+ electrical cabinets in protected area for instrumentation, AMB controllers and variable-frequency drives
(~0.6 x ~2.7 x ~2.2 m3)
 Ground level installation of cabinets under study with 150 m of cabling (today: 25 m max)

## Slide 18: P4 Layout: new cryogenics for SRF module
With interconnection for partial redundancy
(Accepted as baseline)
P4
S34
S45

## Slide 19: P4 cryogenic process & flow diagram
UCB:
6-7 kW @ 4.5 K
cryoplant (tbc)
UX45

## Slide 20: P7 Layout: Deported current feed boxes
  New cooling circuits for SC links and deported current feed boxes
  Extension of the warm recovery lines to the TZ76
  Cryogenic design of new SC links and current feed boxes.
TZ76
S67
S78

## Slide 21: Specific cryogenic studies and tests (or what differ from LHC design ?)
Cooling circuits for large heat deposition:
  on 1.9 K cold masses up to 10 W/m  heat extraction from SC cables and quench energy margin  Generic heat flow in magnet cross section
  on beam-screens up to 13-20 W/m (image current effect ?)
Cooling of HTS SC links and current feed boxes
Cooling and pressure relief of crab-cavities
Validation tests on SC link, crab-cavities, magnets, beam screens…
Reactivation of the Heat Load Working Group
Quench containment and recovery (cold buffering ?)
Large-length cable (150 m) for cold-compressor controls and drives
Large capacity (750-1500 W) sub-cooling heat exchangers
Larger turndown capacity factor on 1.8 K refrigeration cycle: up to 10?
From users to cryogenic infrastructure

## Slide 22: Schedule
: Freeze of heat load requirement
P7
P1&P5
(type A)
P1&P5
(type X)

## Slide 23: Conclusion
Several HL-LHC cryogenic layouts have been presented with alternatives for cooling sectorization and redundancy  decision needed for main sectorization option, additional study needed on detailed options
Preliminary heat load estimate is defined :  local and global limitation for sector cryogenics are compatible with the proposed HL-LHC beam parameter.  the HLWG to refine and follow the heat load inventory have to be reactivated.
Specific cryogenic studies and tests are defined  some of them have already started
Integration study of new underground equipment must be done to validate:  layout and interface requirements of all LSS magnet systems as function of their operation temperature
 the possible reuse of part of the existing distribution system (QRL)  the underground space availability for the cold compressor boxes at P1 and P5