## Slide 1: Some RP constraints, general guidelines
LAGUNA-LBNO layout study group
22/1/2013

## Slide 2: Legislation
Rules are defined in CERNs radiation protection legislation (Safety code F and underlying rules)

## Slide 3: General guidelines
ALARA (optimization) starts already at the design phase
Use ‘correct/good’ materials ... ActiWiz, material catalogue EDMS # 1184236.
Avoid a facility in ‘wet’ areas ... a hydrological study is needed
Perform core sampling before construction
Shielding must not only satisfy limits but must also be optimized (ALARA)
Install only absolute necessary equipment in ‘hot’ areas
Minimize air volumes in ‘hot’ areas or even better use an He environment or best a vacuum environment.
Clear separation of ‘air’ in target area, adjacent areas and the outside; ‘air’ tightness is a key element.

## Slide 4: General guidelines
‘Air’ pressure has to be lowest in the area with the highest radiological risk, higher in adjacent areas and highest outside the facility.
Use a closed ventilation circuit with HEPA filters for ‘air’ inside target area.
Closed cooling circuits for ‘hot’ elements (like target, horn etc.) .. heat exchanger.
Avoid sumps in areas with high concentration of tritium. Don’t install ventilation units next to sumps.
Consider remote maintenance/repair ... residual dose rate is too high for manual interventions
…….