## Slide 1: Maintenance Specificities in the CERN Cooling and Ventilation Group
Asset and Maintenance Management Workshop CERN, 13-15 November 2013
I. El Hardouz, U. Epting, S. Poulsen, G. Peon (CERN EN/CV)

## Slide 2: Summary
Definitions and Acronyms
Introduction to EN/CV
Overview of EN/CV Maintenance
CMMS in EN/CV
Key Performance Indicators
Meter Readings
Conditional Maintenance
Summary
Conclusions

## Slide 3: Definitions and Acronyms
Position
Hierarchical structure
  Parent
  Child
MP: Maintenance Plan
PM: Preventive Maintenance
CM: Corrective Maintenance
WO: Work Order
Notes: Position: place of the installation in which a certain type of equipment has to be hosted
Parent: groups positions of an installation that have a common role

## Slide 4: Equipment Structure
Notes: Reflects the structure of the CMMS

## Slide 5: Introduction to EN/CV
The CV group is responsible for the CERN
Cooling and Ventilation
installations:
DESIGN
WORKS
OPERATION
MAINTENANCE
ACCELERATORS
DETECTORS
EXPERIMENTAL AREAS
COMPUTER CENTER

## Slide 6: Introduction to EN/CV
HVAC:
  Tunnel
  Experimental caverns
  Service caverns
  Pressurized safe areas
  Surface “machine” buildings
  Smoke and Gas Extraction Systems
Water Systems:
  Primary water
  Demineralised water
  Chilled water
  Mixed water
  Reject water
  Sanitary water
  Fire fighting water
Compressed air systems
Electricity
Control and supervision systems
A total of
76000
pieces of equipment

## Slide 7: Cooling and distribution
Cooling towers (450 MW) 22
Chilled water production : 6-12oC (73 MW) 35
Cooling plants (raw water, demineralized water, C3F8, C6F14) 150
Distribution Pipework 800 km
Total water consumption 5'400 m3/h
Equivalent to 10% consumption Geneva Canton

## Slide 8: Ventilation, Fluid Systems
HVAC 1’500 units
from 2’000 to 120’000 m3/h per unit
Fire fighting systems 800 points
Compressed air 14 installations
distribution network 200 km
Demineralised water production 20 m3/h - 0.1 μS/cm

## Slide 9: Overview of EN/CV Maintenance
The general activities are covered by just two contractors
Other particular activities are assigned to specialised contractors, i.e. water treatment
Their work is divided in geographical areas
  PS complex plus 50% of the LHC installations
  SPS complex plus 50% of the LHC installations
Stand by interventions:
  PS, SPS: Contractors
  LHC, CERN Computing Centre: CERN
Maintenance Budget of 6MCHF/yr
Asset Value of 600MCHF

## Slide 10: Organisation of the Preventive Maintenance

## Slide 11: Preventive Maintenance Maintenance Plans
MPs generates WOs at the level of the Parent
The WOs point to Maintenance Procedures according to the equipment installed within the Parent
The MPs automate provisional WO start and end dates

## Slide 12: Organisation of the Corrective Maintenance
Notes: If spare parts missing, contractor communicates in WO
If intervention due to access, safety, length of time is forbidden, contractor communicates in WO

## Slide 13: CMMS in EN/CV
CV utilizes mainly the following modules in INFOR EAM
  Equipment
    Assets
    Positions
    Parts
    Structure
  Stores
    Spare Parts
    Pick Tickets
    Reservation
    Requisition
    Purchase orders
    Parts labelling
    Minimum stocks
  Works
    Work requests Work orders (WO)
    Maintenance plans
    Inspections
    Meter readings

## Slide 14: Information in the WOs
Dates in WOs
  Filled by the system
    Event date: date of WO creation
  Filled by CV personnel
    Requested start date
    Requested end date
  Filled by contractors’ personnel
    Schedule start date
    Schedule end date
    Actual start and end dates
    Request and delivery of spares
Other Information:
  Filled by CV personnel
    Information to assess the work
    Contact person
    Particular safety issues
  Filled by contractors’ personnel
    «Assigned to»
    Booked hours for a particular employee and day
    Description of the work done
    Spare parts used
    Tests carried out
    …

## Slide 17: Main KPI: Contractor Performance

## Slide 18: Main KPIs: Equipment Condition

## Slide 19: Main KPIs : Reactivity

## Slide 20
Main KPIs : Overall performance

## Slide 21: Examples of two KPIs over time

## Slide 22: Meter Readings in the CV group
Meter readings for different equipment
  Air Compressors
  Trane Chillers
Frequency
  Different intervals: e.g. weekly, twice per year
  Configured via Infor EAM PM Schedules
Visualization
  Infor EAM Custom Tab: “Inspections & Readings”
Tools for data entry
  GS-ASE Infor EAM Mobile (Psion handheld)
  EN-CV smartphone application

## Slide 23: Meter Readings: CV Smartphone Application
Webpage application optimised for smartphones
It organizes the data collection by PM Schedule (can comprise equipment of different Classes)
No investment required for proprietary equipment and can be on operators personal device (Bring-Your-Own-Device)
It can also be used from any platform with a Web browser (including Psion Ikon)
It works off-line in areas without GSM/WiFi
It is very responsive

## Slide 24: Meter readings: Ex. Historical data of chiller FCK-00030

## Slide 25
Mechanical revision 40000h and cleaning of a chiller in bldg. 355, 378
… before and after cleaning
bldg. 378

## Slide 26: Conditional Maintenance: Vibration analyses

## Slide 27: Conditional Maintenance: Vibration analyses

## Slide 28: Conditional Maintenance: Vibration analyses

## Slide 29: Conditional Maintenance: Vibration analyses

## Slide 30: Summary
EN/CV utilises the main modules of INFOR EAM
Information entered by the System, CV staff and Maintenance contractors is crucial to assess the different actors in maintenance
CV makes use of tailored made KPI to pinpoint weak and strong points in the Maintenance activities
Particular Meter Readings are valuable information to trigger conditional maintenance in some equipment such chillers and compressors
A specific project has been made for Conditional Maintenance based on Vibration measurements

## Slide 31: Conclusions
Structure of equipment it reduces the intervention time for all the maintenance participants
KPIs, utilised to better monitor the Maintenance Activity and plants condition to:
      Support the decisions by the CERN management
      Take actions by Stores and Operations
      Manage of Contractors
      Repair and improve the installations
Meter readings
  Faster data entry and interpretation of results
  Clearer vision of the equipment utilization over time
Vibration analysis
  Detect risk and allow for intervention before breakdown

## Slide 32: Thank you for your attention!!