## Slide 1
Introduction to the
New Hardware and Software of the
Bake-out Rack
Sebastien Blanchard TE/VSC
Interlocks, Controls and Monitoring Section

## Slide 2
Bake-out Rack, What is it?
Bake-out Recipe/Program
Local User
8 Additional Temperatures for interlocks
Hardware V.2 Only
PID Regulation
Programmable
Logical Controller(PLC)
With Power Relays for
24 Regulation Channels
Heater
Thermocouple
Remote
User
Touch
Panel
Master PLC
PVSS
Server
Profibus
“Machine”
Ethernet
“Labs”
Hardware V.2
Input Interlocks (Clients)
Output Interlocks
(Clients)
NS
SMS Notification
Ethernet
“Labs”
Hardware V.2
Outgassing Bake-out
or NEG Activation Bake-out

## Slide 3
PLC Bake-out Racks, Where?
LHC : LSS & Experiments
LEIR
AD
ISOLDE : Rexebis
Booster : Ion Pumps & Septa
PS:
Ion Pumps & Septa
CTF
Vacuum Labs
&Test Benches
(Bldg 113, 30, 169, 867, 101,…)
SPS:
Beam Diagnostics
TOTAL: 103 Bake-out Racks (PLC), first in 2002
NS

## Slide 4
Bake-out Rack
Hardware V.2 and New Software, Why?
Main New features :
Ultra High Vacuum
Bake-out
Fragile
Equipment
  SAFETY :
  8 Additional Thermocouple channels for Control & Interlock
  Power Cut System: if ‘Error’ Power Relays Circuit Breaker is switched Off
  PERFORMANCE :
  New parameterized PID regulation with auto-tune system
  FLEXIBILITY :
  Number of Recipes/Programs from 6 to 12
  Old Software version is more than 10 years old
Specific
Heating System
&
NS

## Slide 5
Chart: Time (hours)
| 1 | 2 | 3 | 4 | 5 | 6 | 6.5 | 7 | 8 | 9 | 10
Process Value (Reading Temperature) | 20 | 45 | 95 | 145 | 195 | 195 | 150 | 120 | 80 | 50 | 20
Real Temperature w/o Safety System | 20 | 35 | 80 | 130 | 180 | 190 | 250 | 280 | 320 | 340 | 350
Real Temperature with Safety System | 20 | 35 | 80 | 130 | 180 | 190 | 250 | 220 | 160 | 110 | 70
Set Point Temperature | 20 | 50 | 100 | 150 | 202 | 202 | 202 | 202 | 202 | 202 | 202
Safety system
Unexpected Event!
Other Safety functionalities :
  Heater Power Limitation (Software limitation, % of the Max Heater Power)
  Fuse (Hardware limitation)
If
Then “Stop Channel”
Heater
TC
TC
Example:
uncoupled!
NS

## Slide 6
Channel Status (Error Code) |  |  |  |  |  |  |  | ACTION |  |  |  |  |  |  | 
 |  |  |  |  |  |  |  | LEVEL 1 Safety OFF Power Cut OFF |  | LEVEL 2 Safety ON Power Cut OFF |  | LEVEL 3 Safety OFF Power Cut ON |  | LEVEL 4 Safety ON Power Cut ON | 
OK |  |  |  |  |  |  |  | N/A |  |  |  |  |  |  | 
Power 0% |  |  |  |  |  |  |  | N/A |  |  |  |  |  |  | 
Power 100% |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Control Channel Warning |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
∆T > 15ºC |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
∆T > 25ºC |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
TC Open Cable or PV > 900ºC |  |  |  |  |  |  |  | STOP CHANNEL |  |  |  |  |  |  | 
Control Channel Interlock (Error) |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Power 100% (>10 min.) |  |  |  |  |  |  |  | N/A |  | (Switch OFF channel power command) |  |  |  |  | 
Control Channel Interlock overshoot (> 10 min.) |  |  |  |  |  |  |  |  |  |  |  | SHUT DOWN ALL CHANNELS POWER RELAYS |  |  | 
∆T > 50ºC |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
External Interlock 1 or 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
∆T = │Set Point - Process Value │ |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | : No Error/Warning |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | : Warning |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | or |  | : Error |  |  |  |  |  |  |  |  |  |  |  | 
Safety Levels (New Software)
Default Safety Level !
SMS
Notification
Why shutting down all power relays?
In case of a ‘short circuit’ power relay or a cabling inversion, stopping channel will not stop the heater involved
Stopping only one channel may induce dangerous thermal constraints (Ex: Sector Valves)
PLC is always power supplied, local control (touch panel) and remote access are still available during a power relays shutdown.
NS

## Slide 7
New Software : New Regulation
PID ALGORITHM
Touch Panel: Re-Init Panel
Touch Panel: PID Parameters
Don’t worry!
If you don’t want to parameter the rack,
default values (compatible with Standard Bake-out)
are re-initialized when PLC CPU restarts
Tune Request:
Using the point of inflection, the lag time (TU) and process time constant (TA)
the software automatically set the PID parameters.
Use ‘Auto Tune’ only for specific bake-out systems
AUTO TUNE
DEFAULT VALUES
Following values can be parameterized by user
GAIN proportional gain
TI integral time (second)
TD derivative time (second)
D_F derivative factor
(Old software only Proportional GAIN and Derivative factor)
NS

## Slide 8
New Software : Specific Heating system
Courtesy: Yannick Riva / Bernard Henrist
Regulation Performance Improved :
  Less oscillations during step transitions
  Better homogeneity (Old Max∆T> 60ºC New Max∆T < 20ºC)
New Software
And correct PID
parameters
Old Software
Thin Polyimide Heater Tests with Old and New Software
Monitoring Temperatures
all along the Chamber
Monitoring Temperatures
all along the Chamber
Temperature (ºC)
Temperature (ºC)
NS

## Slide 9
Last Slide
  Acknowledgements:
  N. Zelko (Specifications, Tests and Validation)
  Y. Riva / B. Henrist (Tests with Thin Polyimide Heaters)
  L. Kopilov / M. Mikheev / H. Pereira (SCADA/PVSS development)
  Reminder Next Week - 2 Practical Sessions (only registered persons)
  Tuesday 2013-01-22, 2pm
  Thursday 2013-01-24, 2pm
  Conclusion:
  Software:
  Old and new versions of the Bake-out rack, Touch Panel & PVSS interfaces are very similar
  New functionalities → You can choose to use it or not.
  By default the bake-out rack is parameterized in the higher safety level!
  Hardware:
  All Racks Hardware V.1 and V.2 will migrate to the new software before LS1
  Documentation:
  Specifications: https://edms.cern.ch/document/1234501 (Released)
  User’s Guide: https://edms.cern.ch/document/1240938 (In Work)
NS

## Slide 10
Spare Slides
PLC (Siemens)
Touch Panel
Connector
Heaters Output
switches and LEDs
Status LEDs
Heaters Connectors
PC Connector

## Slide 11
Spare Slides
Remote Power Relays
command
Thermocouple connectors
230Vac Outlet
Control/Interlock Thermocouples
PLC
Power Supply
Output Interlocks
Input Interlocks
Ethernet
Connector
Profibus
Connector
Remote Power Relays
Satus LEDs
400Vac Power
Supply
Circuit Breaker

## Slide 12
Spare Slides
PVSS Panel :