## Slide 1: TT10 Remedial works
What is happening

## Slide 2
Compression failure in crown (some cases)
Tension/Shear failure in shoulders (typical)
Compression
Tension

## Slide 3
Failure of Primary and Secondary due to poor ground in crown, or squeezing ground conditions
Failure of Primary and Secondary due to void in crown above secondary
Failure of Secondary due to void or poor concrete in crown (primary fails subsequently due to load increase)
Evidence:
No void found
Concrete thickness and quality ok
Not delineated by secondary lining pour length
Evidence:
Concrete thickness and quality ok
Not delineated by secondary lining pour length
Void found
Evidence:
Poor concrete thickness and quality
Delineated by secondary lining pour length

## Slide 5
Stage 1
Remove shoulder and knee pipework
Remove beam
Slide top cable tray away from wall if possible

## Slide 6
Stage 2
Place invert channel section
  152 x 152 x 37 section
  1m Centres

## Slide 7
Stage 4
Place axis steel bar sections
  40 x 150 section
  1m Centres
Shear connection with invert channel

## Slide 8
Stage 5
Place Shoulder I Beam
  152 x 152 x 37 section
  1m Centres
Shear connection with axis channels
Pre-stress I beam

## Slide 9
Stage 6
Place Crown I Beam
  127 x 76 x 13 section
  4no. in crown
Connect crown fill formwork to I beam
Cementitious grout behind former
Formwork (steel plate)
Cementitious Grout
Existing Lining (Cracked and displaced)
Potential Void

## Slide 10
Stage 6
Drill through grout and old linings and low pressure grout to fill voids above crown

## Slide 11
Stage 7
Install false floor over inert channel

## Slide 12
Stage 8
Reinstate Beam and pipework

## Slide 13: Planning