## Slide 1
For the Safety Folder + Environmental impact Study
Simple process:
Identify Safety issues >> description >> risk analysis > (at different project phases)
              controls, procedures, barriers, equipment…
              (some are choices, some requirements are imposed)
Many “standard” hazards will be treated with CERN normal rules on: electricity, heights, etc.
Major “new” hazards are Cryogenics and gas handling.
Installation: build and equipment quality: records, tests...for safety clearance by HSE.
Operation: methods and procedures, leaks and losses, accidents.
Small Argon leaks impose constant evacuation of all lower levels, ODH detection, training…
Safety vents need to be ducted out of the building, and designed for regular testing..
Accidents and larger leaks impose emergency plans; we need to identify the “most credible incidents”, and from the estimated gas or liquid losses, the safe distances can be calculated, the size of emergency ventilation and other controls.

## Slide 2
Earthquake:
Cryostat design and manufacture to EU building standards: 5.5- 6.1 Richter, 15 seconds.
EDMS 1158454
A large risk of gas accidents is from handling:
Gas bottles, tanker deliveries, crane manipulations.
Preventive measures:
gas points outside buildings, gas piped in
Delivery point access and layout secure
Hazardous and delicate cryo equipment protected.
Mitigation measures:
Easy access to safe escape passage (distance depends on “credible incident” details)
Emergency ventilation extraction (possibly heated)
Options and details have to be workable for the experiments too.
And equipment failures: welds, pipes valves, etc.

## Slide 3
Actions
Identify a set of most credible incidents (starting with the LNGS study)
Risk analysis and control measures with HSE and CERN Cryo safety expert.
Specify Mitigation measures where needed.
This inputs into the integration plans for end of August.