## Slide 1: Kicker Electronic and Slow Control
Etienne CARLIER AB/BT/EC

## Slide 2: Outline
Control Architecture
State Control and Surveillance System
Trigger Synchronisation & Distribution System
Beam Energy Tracking System
Operational Check

## Slide 3: Architecture General
State
Kick Time
Kick Strength
State Control & Surveillance System SCSS
Trigger Synchronisation & Distribution System TSDS
Beam Energy Tracking System BETS
Alarm
Logging
Trending
Operational Check Static & Pulse modes
Fast Analog Acquisition System

## Slide 4: Architecture Functional
Power Supplies
Power Triggers
Pulse Generators & Kicker Magnets
Re-Trigger
1
1
1
1
15
15
15
15
Beam Energy Tracking System
State Control and Surveillance System
Trigger Synchronisation and Distribution System

## Slide 5: Performance of LHC Extraction Kickers Typical Possible Failures
Generator failure in static mode  SCSS
  Less than 15 pulse kickers are able to respond to a dump request
Energy tracking failure  BETS
   Kick strength outside tolerance window
    Kick is too large
    Kick is too small
Synchronisation failure  TSDS
   A spontaneously triggering of a kicker
  A drift or shift of the synchronisation pulse train w.r.t. the beam abort gap
Generator failure in pulse mode  POC
   One missing branch

## Slide 6: State Control & Surveillance
State management
Interlock
  Switches
  Power supplies (over-voltage, over-current, short-circuit
  Electrical circuit closure…
Monitoring
  Power supply (current, voltage)
  HV dividers…
Personal Safety
Electrical distribution
State
Kick Time
Kick Strength
State Control & Surveillance System
Trigger Synchronisation & Distribution System
Beam Energy Tracking System

## Slide 7: State Control & Surveillance Architecture
PROFIBUS-DP PROFIsafe
DP / DP Coupler
CP416F-2DP
Ethernet
Simatic S7-400
S7-300 modules used in standard mode
S7-300 fail-safe modules used in safety mode
Generator 15
PROFIBUS-DP PROFIsafe
ET200M
ET200M
Simatic S7-300
CP315F-2DP
Generator 1
PROFIBUS-DP PROFIsafe

## Slide 8: State Control & Surveillance Implementation
Based on fail-safe SIEMENS SIMATIC S7-F Programmable Logic Controllers and on fail-safe communications between PLC via PROFIBUS-DP fieldbuses using PROFIsafe protocol.
  Surveillance based on a hierarchical design based on failure severity
Analogue inputs based on redundant 4-20mA current loop sensors, digital inputs based on non-equivalent sensors and redundant digital outputs used for actuators control.
  “Passivation” of inputs and outputs (i.e. dump request) in case of sensor failure or discrepancy between sensors (redundant, non-equivalent)
  Manual “Re-integration” after a failure involving a safety elements
  Reaction time is typ. 20ms (max 50ms)

## Slide 9: Trigger Synchronisation & Distribution
State
Kick Time
Kick Strength
State Control & Surveillance System
Trigger Synchronisation & Distribution System
Beam Energy Tracking System
Synchronisation of dump requests with beam abort gap
Distribution of dump requests up to HV generator
Protection of the machine against spontaneous firing
State management
Interlock
  Switches
  Power supplies (over-voltage, over-current, short-circuit
  Electrical circuit closure…
Monitoring
  Power supply (current, voltage)
  HV dividers…
Personal Safety
Electrical distribution

## Slide 10: Trigger Synchronisation & Distribution Architecture
Fault-tolerant
Fail-safe
Re-trigger lines
Branch A
Branch B
Branch A
Branch B
Generator 1
Generator 15
TFO
TFO
Trigger Fan-out
PTU
PTU
PTU
PTU
Power Trigger Unit
RTB
RTB
RTB
RTB
Re-trigger Box
RTD
Re-trigger Delay
TSU
TSU
Client Interface
Frev
Trigger Synchronisation Unit

## Slide 11: Trigger Synchronisation & Distribution Dump Request Distribution
Energy required to distribute the dump request up to the kicker HV generator is
  Pre-stored within capacitor at each stage of the triggering chain,
  Used to trigger the next stage, and
  Checked before a beam permit signal is issued,
But, somebody has to trigger the chain… to push the first domino stone!
 Interface to the LBDS Clients
Propagation of the trigger pulse through the different stages of the triggering chain relies either on an active fail safe logic up to the synchronisation with the abort gap and on a passive redundant fault tolerant logic up to the HV generator in order to avoid asynchronous beam dumps.
Dump request uses the “domino effect” for trigger distribution

## Slide 12: Trigger Synchronisation & Distribution LBDS Clients
BIS
8.315 MHz & 9.315 MHz Frequencies
BLM
BETS
LBDS MKD Ready MKB Ready TSU Ready BETS Ready IPOC Ready LASS Ready
Yes
Non-Ambivalent Redundant Contact
(SCSS)
Client
No
Yes
Yes
Current Loop
10 MHz Frequency
Fibre Optic
< 250 ns
Opto-coupled copper cable
< 1 us
50  galvanic signal
< 250 ns
Floating Relay
~ 20 ms
Signal Redundancy
Response Time
Signal Media
Signal Type
Injection Prepulse
No
1us logic pulse
50  galvanic signal
< 150 ns

## Slide 13: Trigger Synchronisation & Distribution Implementation
1oo2 ‘Trigger Synchronisation Unit’ systems can synchronise the dump request.
  Both systems are independent.
  The mission time for tests is 89 µs.
1oo4 independent trigger channels can issue the dump trigger.
Each branch has 5 re-trigger sources which feed 2 re-trigger distribution lines.
  Twice 1oo5.
  Each source can deliver sufficient energy to trigger all power triggers of all magnets MKD/MKB.
Continuity of the re-trigger lines is continuously checked (pulse train).

## Slide 14: Beam Energy Tracking
State
Kick Time
Kick Strength
State Control & Surveillance System
Trigger Synchronisation & Distribution System
Beam Energy Tracking System
Acquisition and distribution of the beam energy
Generation of kick strength reference signals
Surveillance of the charging voltages w.r.t. the beam energy
Synchronisation of dump requests with beam abort gap
Distribution of dump requests up to HV generator
Protection of the machine against spontaneous firing
State management
Interlock
  Switches
  Power supplies (over-voltage, over-current, short-circuit
  Electrical circuit closure…
Monitoring
  Power supply (current, voltage)
  HV dividers…
Personal Safety
Electrical distribution

## Slide 15: Beam Energy Tracking System Functions
Acquisition of the machine “beam energy”,
Generation of the kick strength reference signals for LBDS extraction and dilution kicker high voltage generators w.r.t. the beam energy,
Continuous surveillance that the charging voltages of the different capacitors within the kicker high voltage generators follow their references within predefined tolerance windows (extraction trajectory aperture),
Continuous surveillance that the LBDS extraction septa and ring quadrupole Q4 currents are within predefined tolerance windows (extraction trajectory aperture),
Generation of a dump request after detection of an upcoming tracking fault if the measured values are not within predefined tolerance windows relative to the beam energy,
Distribution of the beam energy to external clients.

## Slide 16: Beam Energy Tracking System Relations
Beam
dump
Other users
DCCT
Dipole Magnet 4-5
Power Converter Right 4
DCCT
Dipole Magnet 5-6
Power Converter Left 6
DCCT
Dipole Magnet 7-8
Power Converter Left 8
DCCT
Dipole Magnet 6-7
Power Converter Right 6
DCCT
Septum Magnet Beam 1
Power Converter Septum Beam 1
DCCT
Quadrupole Q4 Beam 1
Power Converter Q4 Beam 1
HVD
Kicker Magnet Ext. Beam 1
Kicker HV Gen. Ext. Beam 1
Kicker Magnet Dilution Beam 1
Kicker HV Gen. Dilution Beam 1
Beam Energy Tracking System
(BETS)
HVD

## Slide 17: Beam Energy Tracking System Architecture
Main
Bends
ImeasA
EbeamA
UrefKi
Kicker HV
Generators
Beam Energy Meter
Main
Bends
Imeas B
EbeamB
UmeasKi
Kicker HV
Generators
EbeamKi
Tracking Interlock Logic
|EbeamB – EbeamKi| > 0.5% * EbeamB
Dump Trigger Request
Beam Energy Meter
Beam Energy Meter
Reference
Interlock
Acquisition
Settings
Acquisition
Tracking

## Slide 18: Beam Energy Tracking System Implementation
Based on four redundant and independent measurements of the main bends magnet current to get the beam energy.
Generation of the kick strength reference signals is integrated within the SCSS.
Tracking interlock logic is based on two redundant systems built on the basis of two different technologies
  One on fail-safe SIEMENS SIMATIC S7-F Programmable Logic Controllers  Feedback Tracking
  The other one on dedicated hardware  Real-time Tracking
Both systems have to be continuously in agreement. In case of discrepancy between the two systems, a dump request will be issued immediately.

## Slide 19: Beam Energy Tracking System Real-Time Vs Feedback
Dedicated VME hardware
Surveillance of
  MKD
    Principal circuit
    Compensation circuit
  MKB
  Q4
  MSD
1 ms surveillance cycle
10 µs response time
Dump request through redundant 10 MHz connections to the TSU
Integrated within SCSS
Surveillance of
  MKD
    Principal circuit
    Compensation circuit
    Triggering circuits
  MKB
20 ms surveillance cycle
10 ms response time
Dump request through the general “LBDS ready” signal
Real Time Tracking
Feedback Tracking

## Slide 20: Post-Operational Check
Post-Operationnal analysis is the only way to verify the correct execution of the last dump action.
Despite a perfectly dumped beam, it remains possible that damage has been caused to one or more components of the dump system during the previous dump action (e.g. the solid state switches).
The beam dump system will be declared ready for the next mission if, and only if, it can be expected that all the hardware, including all the redundant components, will respond correctly to the next dump request.

## Slide 21: Post-Operational Check Data Acquisition
Trending
  Continuous sequential data logging at a fixed acquisition frequency
Alarm
  Acquisition and archiving of unforeseen process events detected by equipment surveillance programs
Transient Recording
  Pre & Post trigger data acquisition after reception of an external asynchronous trigger
Logbook
  Record of actions performed on equipment hardware and software by CCC and equipment specialists

## Slide 22: Post-Operational Check Transient Signals
Principal Switches
Currents
Compensation Switches
Currents
Free wheel Diodes
Currents
Magnet Current

## Slide 23: Post-Operational Check Transient Recording Analysis
Two different levels of Analysis
  XPOC – External Post Operation Check
    What happened during the dumping process with the beam?
    What is the evolution of the performance of the system
  IPOC – Internal Post Operation Check
    How performed the different sub-systems during the dumping process?
IPOC analysis for LBDS extraction kicker
  Kick Synchronisation Analysis
    Kick rise-time, kick length,
    Kick synchronisation with beam.
  Kick Amplitude Analysis
    Kick normalization with beam energy
    100 % kick measurement,
    Kick first overshoot, second overshoot.

## Slide 24: Post-Operational Check Implementation
High precision acquisition and analysis of the 15 magnet current pulse shapes will be performed after each dump action.
  2 different types of acquisition sensors: Pearson PU (passive) and Rogowski PU (active)
The acquisition system is based on two CompactPCI crates running SCL4 and housing:
  NI-PXI 5122 digitizers with 14 bit resolution and 100 MS/s sampling rate for the kick strength & kick synchronisation surveillance and monitoring
Acquisition and verification of the current in the different branches of the generator in order to identify the faulty circuit will be available in a second phase (prototype available)
  Principal circuit
  Compensation circuit
  Freewheel circuit