## Slide 1
Linac4 Ion Source –
Safety Aspects HT, Gas, Cs, Electrical, Fire
1
A. Funken – J. Lettry
On behalf of the Ion Source team
L4 Ion Source Review
14.11.2013
CERN

## Slide 2: Outline
Hazards inventory
Risk control measures
Safety documentation
Conclusion and outlook

## Slide 3: Hazards inventory
Electrical hazards:
High voltage (10kV to 50 kV)
Capacitor banks (20J/50 kV)
Non ionizing radiations:
High power RF 2 MHz (RF power amplifier in the Klystrons hall)
Flammable gas:
Hydrogen (2 x 10 liter 200 bar gas bottles)
Chemical hazards:
Oil
Caesium (with plasma Cs source)
Mechanical hazards:
Pressurized pipelines (0.5-3 bars H2)
Closed Faraday cage
1
2
3
5
Electrocution, electrical shocks, fire
Electrical shocks, tissue burns
Explosion, fire
Release of gas, explosion; hearing loss, material projection
Fire, explosion, intoxication, chemical burns
Pollution
NY03
NY04
NY05
NYTR
NJ01
NY08
1
1
5
5
Equipment under vacuum (up to 10-7 mbars)
2
3
4
4

## Slide 4: Risk control measures
Based on HSE Launch Safety Agreement (equivalent to EDMS 1218116 for Linac4 ion source):
This document is an overview of the applicable Safety requirements for the ion source (based on the CERN Safety rules or if not existing, on Host States
regulations, European Directives, international standards and best practices).
Fields | Safety requirements
Electrical safety | Safety Code C1- Electrical safety code Safety Instruction IS24 – Regulation applicable to electrical installations
Non ionizing radiations (RF) | European Directive 2013/35/EU French Decret n˚2002-775 of 3 Mai 2002
Flammable gas (H2) | Explosive atmospheres (GS-C2)
Mechanical safety (Pressure, vacuum) | Safety Regulation on mechanical equipment (SR-M) General Safety Instruction (GSI-M2) – Standard pressure equipment
Chemical safety (Cs) | Safety Regulation on chemical agents (SR-C) General Safety Instruction (GSI-C1) on prevention and protection measures General Safety Instruction (GSI-C3) on monitoring of exposure to hazardous chemical agents in workplace atmospheres
Notes: Measures taken to remove or mitigate the risks.

## Slide 5: Risk control measures
Electrical safety and RF
Equipment are located inside the closed Faraday cage having a protection index IP3X according to IEC60529.
Faraday cage equipped with AUL (local emergency stop)
Linac4 tunnel equipped with AUG (general emergency stop)
Faraday cage equipped with an access interlock system (EDMS 1212106), PLC-based.
In case of access, the high-voltage power converters and the 2 MHz RF generator are disabled. Racks automatically grounded. Warning signs posted on the doors indicating that access is restricted to specialists.

## Slide 6: Risk control measures
The maximum volume of a hydrogen leak is 2 m3 with one gas bottle (the full content of one 10 liter, 200 bar bottle).
The ventilation system is supervised from the CCC.
In case a failure of the ventilation system, the standby service is called (specific written procedures).
The gas rack itself is classified as ATEX zone 2, in line with Safety Guideline C-2-0-3.
In case of a gas leak: the ventilated volume around the ion source is considered as large enough (2’500 m3) so that no explosive hazards can arise outside the rack. Hence, gas detection system is not necessary.
Flammable gas safety
The gas distribution system can be fully vented with clean nitrogen so that no flammable gas will remain in the system at the operational state “Stop”.
Explosion risk assessment: EDMS 1261469
Notes: Zone 2: A hazardous area in which an explosive atmosphere consisting of a mixture with air of flammable substances in the form of gas, vapour or mist is not likely to occur in normal operation but, if it doe
Here, ‘not likely to occur in normal operation, but if it does occur, will persist for a short period only’, is taken to mean a few times per year, of a duration of about 30 minutes each time (< 10 hours per year in total). s occur, will persist for a short period only.

## Slide 7: Risk control measures
All sections of the pipe work are protected by safety relief valves (relief pressure: 5 bar), with exhaust into the tunnel, which are subjected to periodic tests by the HSE.
All the components and the assembly of the gas system are made and tested according to the General Safety instruction GSI-M2 for standard pressure equipment, EDMS 875610.
Mechanical safety
The pipe work is tested to 1.5 times the nominal pressure.
Flow rate measures by two redundant flow meters which, in case of abnormal flow rate automatically, will close two pneumatic safety valves.
Extract from the Explosion risk assessment file,
EDMS 1261469
Pressurized pipelines
Equipment under vacuum
EN-MME design

## Slide 8: Risk control measures
Fire safety
Faraday cage
Tunnel
Fire detection system : activation of one detector triggers a level-3 alarm and the intervention of the fire brigade
Smoke extraction system (started by the fire brigade)
Evacuation plans posted on site
Fire extinguishers and
fire-fighting system (RIA)
Fire alarm (evacuation) in case of activation of two fire detectors
Interlocks with the ventilation system
Fire detection system + Fire alarm

## Slide 9: Risk control measures
Chemical safety
Monitoring of oil pressure, temperature, levels includes in the interlock chain of the power converters.
Oil
1
1
The transformers of the three HV pulsed power converters are immersed in oil:
Sealed oil tanks
Oil type MIDEL 7131 (3 x 95L): not toxic, high fire point (> 300˚C)
100L retention bund at rack bottom

## Slide 10: Risk control measures
Chemical safety
Chemical risk assessment (to be released).
Specific procedures to handle the caesium in Linac4 (In Work): installation, multi month operation and exchange of Cesiated ion sources.
Caesium
(Quantity in the LINAC4 source: 100 mg to 5 g)
The Cs-load and condensed Cs vapours are confined within the dispenser and the ion source vacuum tanks.
Coupling the Cs-dispenser to the source will be done according to a procedure.
Maintenance of the component inside the vacuum tank will be done in a dedicated laboratory (Cs-test stand – building 357).
All transport will be under inert atmosphere enclosed in dedicated hoods.
Personnel protective equipment is foreseen (gloves, goggles) and will be adapted to the tasks.

## Slide 11: Safety documentation
The safety documentation is included in the Safety Folder of Linac4 which consists of 4 main parts:
Parts | Contents | Ref. EDMS | Status
Descriptive | Description of the facility in terms of safety, access modes, dismantling and disposal | 1227231 | Approval process closed
Demonstrative | Hazards inventory, risks induced, risk control measures, risk assessments | 1280742 | Under Engineering Check
Operational | Inventory of information notes, operational instructions and procedures related to safety, description of the project phase and organisation | 1280745 | In Work
REM (Record, Experience, Monitoring) | Inventory of all feedbacks, inspections, safety reports, non-conformities, near-misses, incidents, accidents and experience gained | 1280750 | In Work

## Slide 12: Safety documentation
Procedures | Released | To be released | In work
High voltage safety and Interlocks of the Linac4 Ion Source Test Procedure | EDMS 1314944 |  | 
Access and work in the H- source cage |  | X | 
Safety lock-out of the Ion Source power converters |  | X | 
Fire brigade emergency intervention |  |  | X
Procedure in case of failure of the ventilation system of the Linac4 tunnel |  | X | 
Replacement of the H2 bottle | EDMS 1261469 |  | 
Emergency procedure in case of problem during operation of the LINAC4 gas system | EDMS 1320768 |  | 
Operation instruction of the gas system: how to connect remotely | EDMS 1320770 |  | 
Caesium related procedures |  |  | X
Status of the safety procedures for the Linac4 ion source:

## Slide 13: Conclusion and outlook
All systems are being documented within CERN safety rules and regulations.
Manpower needs for the remaining safety documentation:
IS-02 (plasma Cs-surface) : 2 months, 0.5 FTE
IS-03 (Magnetron) : 4 months, 0.5 FTE

## Slide 14: Thank you for your attention