## Slide 1: Almost 40 years of operation with tetrodes in the CERN-SPS
CWRF workshop 2014, Trieste
Eric Montesinos, CERN-RF, on behalf of RF-SPS team

## Slide 2: What is the CERN-SPS ?
SPS
1976 (7 km)

## Slide 3: RF in the SPS
1970
2020
2000
1990
1980
2010
1972
prototype Siemens Amplifier
RS2004 tetrode
137.5 kW CW @ 200.2 MHz

## Slide 4: RF in the SPS
1974
First Siemens Transmitter
1 x RS2004 Driver
4 x RS2004 Finals
Total output power = 515 kW CW
1970
2020
2000
1990
1980
2010

## Slide 5: RF in the SPS
1976
Three Siemens Transmitters
3 x 515 kW CW
1970
2020
2000
1990
1980
2010

## Slide 6: RF in the SPS
1978
prototype Philips Amplifier
YL1530 tetrode
35 kW CW @ 200.2 MHz
1970
2020
2000
1990
1980
2010

## Slide 7: RF in the SPS
1980
2 Siemens Lines
20 x RS2004
2 x 1 MW CW
2 Philips Lines
72 x YL1530
2 x 1 MW CW
1970
2020
2000
1990
1980
2010

## Slide 8: RF in the SPS
2 x 4 sections
2 x 5 sections
Travelling Wave
Cavities
Per TWC:
2 x 2 x 375 kW Fundamental
Power Couplers
2 x 500 kW
Power Loads
1970
2020
2000
1990
1980
2010

## Slide 9: First period 1976-1988
Fixed Target & Collider operation
Maximum power 450 kW CW
SPS
1976 (7 km)
North Area
West Area
1970
2020
2000
1990
1980
2010
Chart: Maximum Power
| CW | 43 kHz | 172 kHz
Column1 | 450 | 0 | 0

## Slide 10: Second period 1989-2000
1989-2000: FT + leptons injector for LEP
Maximum power 600 kW CW
+ 600 kW 172 kHz (1994-2000)
SPS
1976 (7 km)
North Area
LEP
1989 (27 km)
1970
2020
2000
1990
1980
2010
Chart: Maximum Power
| CW | 43 kHz | 172 kHz
Column1 | 600 | 600
West Area

## Slide 11: Third period 2001-2005
2001-2004: FT operation
Maximum power 600 kW CW
+ 600 kW 172 kHz (2003)
SPS
1976 (7 km)
North Area
West Area
1970
2020
2000
1990
1980
2010
Chart: Maximum Power
| CW | 43 kHz | 172 kHz
Column1 | 600 | 600

## Slide 12: Fourth period 2006-2013
2006-2013: protons & ions operation + CNGS + injector for LHC
Maximum power 600 kW CW
+ 600 kW 43 kHz (2007-2012)
SPS
1976 (7 km)
North Area
CNGS
2006
LHC
2008 (27 km)
1970
2020
2000
1990
1980
2010
Chart: Maximum Power
| CW | 43 kHz | 172 kHz
Column1 | 600 | 600

## Slide 13: Power request 1976-2018
1970
2020
2000
1990
1980
2010
Chart: 
| 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
CW | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
43 kHz | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 1000 | 1000 | 1000 | 1000
172 KHz | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 1000 | 1000 | 1000 | 1000

## Slide 14: Tubes statistics
Chart: YL1530 SPS 200 MHz, 2 x 32 tubes in parallel
| 1 y | 2 y | 3 y | >= 4 y
Series 1 | 12 | 13 | 30 | 42
Series 2 | 59
Series 3 | 39
Series 4 | 38
Series 5 | 21
Total 1980-2013 : 254 tubes
Average lifetime : 32’000 hours
Tubes with > 28’000 hours : 78 %
(also true for tubes stored 20 years !)

## Slide 15: Amplifiers statistics
Chart: 
| Loss of emission | Input reflections | Unknown | Over temp | Arcing
Reason of fault | 99 | 97 | 20 | 20 | 18
Reason of fault | # of faults | % of faults
Loss of emission | 99 | 39
Input reflections | 97 | 38
Unknown | 20 | 8
Over Temp | 20 | 8
Arcing | 18 | 7
Unpredictable : 23 %
Graceful degradation : 77 % (possible to monitor and predict)
Graceful operation : 99.5 % (2012)
YL1530 SPS 200 MHz, 2 x 32 tubes in parallel

## Slide 16: Operating with ‘OFF Line’ Tubes
In normal operation, one tube delivers 600 kW / 8 = 75 kW
Systems have been designed (1976) to deliver full voltage into the cavity even with 3/4 + 3/4 tubes
In case of two tubes ‘OFF Line’, remaining tubes shall deliver 75 kW x (8/6)^2 = 133 kW
RS2004 tubes are rated 137.5 kW, just ok
P
2P
2P
2P
2P
4P
4P
8P
Pout 3dBCombiner = (A+B)/2 + SQRT(A.B)

## Slide 17: Operating with ‘OFF Line’ Tubes
P
2P
0.5P
0.5P
2P
2.25P
2.25P
4.5P
Pout 3dBCombiner = (A+B)/2 + SQRT(A.B)
In normal operation, one tube delivers 600 kW / 8 = 75 kW
Systems have been designed (1976) to deliver full voltage into the cavity even with 3/4 + 3/4 tubes
In case of two tubes ‘OFF Line’, remaining tubes shall deliver 75 kW x (8/6)^2 = 133 kW
RS2004 tubes are rated 137.5 kW, just ok

## Slide 18: Operating with ‘OFF Line’ Tubes
The same philosophy applies to Philips amplifiers, in normal operation, one tube delivers 600 kW / 32 (+ 3 dB combiner losses) = 20 kW
In case of 2 x 4 tubes ‘OFF Line’, remaining tubes shall deliver 20 kW x (32/24)^2 = 36 kW
YL1530 tubes are rated 37 kW
32P
18P

## Slide 19: Operating with ‘OFF Line’ Tubes
Along the year we loose
  6 Siemens tubes
  16 Philips tubes
Thanks to the graceful degradation and the OFF line possibility we change these tubes during the ‘one day technical stop’ every 8 weeks
We sometimes operate Philips plant with one ‘OFF line tube’
We rarely need to use it with the Siemens plant, but from time to time it helps us to remain available
Even if we operate with faulty tubes, we still have some margin in power
So, we apply the rule
-5% Ufilament → +25% lifetime
I cannot say if the rule is true, I can simply say that our tubes have a very long lifetime
Please keep it in mind looking at our tubes statistics

## Slide 20: Major events 1970-2010
1970-1980
  Development phase + first operation, no major troubles
1980-1990
  No major troubles
1990-2000
  HVPS 18 KVAC capacitor explosion
  Fundamental Power Coupler failures
  Power Load failures
2000-2010
  Near miss Tunnel ceiling water infiltration
  Crowbar/water pipe failure
  HVPS Transformer failure
Local / Remote Control
Miscellaneous

## Slide 21: HVPS 18 KV-AC capacitor explosion
Spring 1997, after few weeks of operation, explosion of a HVPS (18 kV-AC capacitor)
Fire in the cubicle
Mercury crowbar system vaporised
SPS stopped for 3 months
1970
2020
2000
1990
1980
2010

## Slide 22: HVPS 18 KVAC capacitor explosion
Spring 1997, after few weeks of operation, explosion of a HVPS (18 kV-AC capacitor)
Fire in the cubicle
Mercury crowbar system vaporised
SPS stopped for 3 months
1970
2020
2000
1990
1980
2010

## Slide 23: Fundamental Power Couplers
Ceramic failures with the Fundamental Power Couplers
  1994
  1998
  1999
We made a new design, more powerful, based on a Thales klystron disk window, still in operation
1970
2020
2000
1990
1980
2010

## Slide 24: Fundamental Power Couplers
Ceramic failures with the Fundamental Power Couplers
  1994
  1998
  1999
We made a new design, more powerful, based on a Thales klystron disk window, still in operation
1970
2020
2000
1990
1980
2010

## Slide 25: Fundamental Power Couplers
Ceramic failures with the Fundamental Power Couplers
  1994
  1998
  1999
We made a new design, more powerful, based on a Thales klystron disk window, still in operation
1970
2020
2000
1990
1980
2010

## Slide 26: Power load window failure
After 20 years of operation, we had three failures with the window of our power loads
  First one on the Siemens amplifier (1998)
  Two on the cavities (1999)
We made a new design, without a molybdenum junction, thanks to new brazing possibilities
1970
2020
2000
1990
1980
2010

## Slide 27: Power load window failure
After 20 years of operation, we had three failures with the window of our power loads
  First one on the Siemens amplifier (1998)
  Two on the cavities (1999)
We made a new design, without a molybdenum junction, thanks to new brazing possibilities
1970
2020
2000
1990
1980
2010

## Slide 28: Power load window failure
After 20 years of operation, we had three failures with the window of our power loads
  First one on the Siemens amplifier (1998)
  Two on the cavities (1999)
We made a new design, without a molybdenum junction, thanks to new brazing possibilities
1970
2020
2000
1990
1980
2010

## Slide 29: Near miss coaxial lines
During the 2005 one year shutdown, we had to repair the vault above the cavity#2
(water infiltration)
Some of the vacuum seals on the cavity were damaged
The coaxial lines were about to be perforated
1970
2020
2000
1990
1980
2010

## Slide 30: Near miss coaxial lines
During the 2005 one year shutdown, we had to repair the vault above the cavity#2
(water infiltration)
Some of the vacuum seals on the cavity were damaged
The coaxial lines were about to be perforated
1970
2020
2000
1990
1980
2010

## Slide 31: Near miss coaxial lines
During the 2005 one year shutdown, we had to repair the vault above the cavity#2
(water infiltration)
Some of the vacuum seals on the cavity were damaged
The coaxial lines were about to be perforated
1970
2020
2000
1990
1980
2010

## Slide 32: Near miss coaxial lines
During the 2005 one year shutdown, we had to repair the vault above the cavity#2
(water infiltration)
Some of the vacuum seals on the cavity were damaged
The coaxial lines were about to be perforated
1970
2020
2000
1990
1980
2010

## Slide 33: Crowbar/water pipe
Two faults with the same symptoms
  New GTO crowbar system unstable (10 kV)
  A water pipe intermittently arcing between HVDC and GND triggering the crowbar
It took us a long time to fix these, explanation for bad statistics during 2008 to 2010
Ug2
1970
2020
2000
1990
1980
2010

## Slide 34: Crowbar/water pipe
Two faults with the same symptoms
  New GTO crowbar system unstable (10 kV)
  A water pipe intermittently arcing between HVDC and GND triggering the crowbar
It took us a long time to fix these, explanation for bad statistics during 2008 to 2010
1970
2020
2000
1990
1980
2010

## Slide 35: Crowbar/water pipe
Two faults with the same symptoms
  New GTO crowbar system unstable (10 kV)
  A water pipe intermittently arcing between HVDC and GND triggering the crowbar
It took us a long time to fix these, explanation for bad statistics during 2008 to 2010
1970
2020
2000
1990
1980
2010

## Slide 36: Crowbar/water pipe
Two faults with the same symptoms
  New GTO crowbar system unstable (10 kV)
  A water pipe intermittently arcing between HVDC and GND triggering the crowbar
It took us a long time to fix these, explanation for bad statistics during 2008 to 2010
1970
2020
2000
1990
1980
2010
Chart: % SPS down time
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
% RF faults | 0.59 | 0.61 | 0.83 | 0.45 | 1.8 | 1.41 | 1.1 | 0.81 | 0.48 | 0.3

## Slide 37: HVPS Transformer failure
We had two majors faults with the HV transformers
2012 near miss
  one connection of the coil started to burn
  We exchange the transformer before any accident
  Transformers have a lifetime and replacement must be correctly scheduled on old machines
2013
  Measuring cable connection broke and 18 kVAC accidentally touched GND
1970
2020
2000
1990
1980
2010

## Slide 38: HVPS Transformer failure
1970
2020
2000
1990
1980
2010
We had two majors faults with the HV transformers
2012 near miss
  one connection of the coil started to burn
  We exchange the transformer before any accident
  Transformers have a lifetime and replacement must be correctly scheduled on old machines
2013
  Measuring cable connection broke and 18 kVAC accidentally touched GND

## Slide 39: HVPS Transformer failure
1970
2020
2000
1990
1980
2010
We had two majors faults with the HV transformers
2012 near miss
  one connection of the coil started to burn
  We exchange the transformer before any accident
  Transformers have a lifetime and replacement must be correctly scheduled on old machines
2013
  Measuring cable connection broke and 18 kVAC accidentally touched GND

## Slide 40: HVPS Transformer failure
1970
2020
2000
1990
1980
2010
We had two majors faults with the HV transformers
2012 near miss
  one connection of the coil started to burn
  We exchange the transformer before any accident
  Transformers have a lifetime and replacement must be correctly scheduled on old machines
2013
  Measuring cable connection broke and 18 kVAC accidentally touched GND

## Slide 41: Local/Remote control
Local electronics are still the same since the beginning, faults are very rare (electricians of the team are able to repair it)
Remote systems had to be upgraded as not robust enough (specialists needed)
  1970-1991 Nodal
  1991-2013 Siemens S5
  2014-… Beckoff
1970
2020
2000
1990
1980
2010

## Slide 42: Local/Remote control
Local electronics are still the same since the beginning, faults are very rare (electricians of the team are able to repair it)
Remote systems had to be upgraded as not robust enough (specialists needed)
  1970-1991 Nodal
  1991-2013 Siemens S5
  2014-… Beckoff
1970
2020
2000
1990
1980
2010

## Slide 43: Local/Remote control
Local electronics are still the same since the beginning, faults are very rare (electricians of the team are able to repair it)
Remote systems had to be upgraded as not robust enough (specialists needed)
  1970-1991 Nodal
  1991-2013 Siemens S5
  2014-… Beckoff
1970
2020
2000
1990
1980
2010

## Slide 44: Local/Remote control
Local electronics are still the same since the beginning, faults are very rare (electricians of the team are able to repair it)
Remote systems had to be upgraded as not robust enough (specialists needed)
  1970-1991 Nodal
  1991-2013 Siemens S5
  2014-… Beckoff
1970
2020
2000
1990
1980
2010

## Slide 45: Local/Remote control
Local electronics are still the same since the beginning, faults are very rare (electricians of the team are able to repair it)
Remote systems had to be upgraded as not robust enough (specialists needed)
  1970-1991 Nodal
  1991-2013 Siemens S5
  2014-… Beckoff
1970
2020
2000
1990
1980
2010

## Slide 46: Miscellaneous
We had several troubles with usual suspects
  HV wiring
  High Power transmission line connections
1970
2020
2000
1990
1980
2010

## Slide 47: Miscellaneous
We had several troubles with usual suspects
  HV wiring
  High Power transmission line connections
1970
2020
2000
1990
1980
2010

## Slide 48: Miscellaneous
We had several troubles with usual suspects
  HV wiring
  High Power transmission line connections
1970
2020
2000
1990
1980
2010

## Slide 49: Miscellaneous
We had several troubles with usual suspects
  HV wiring
  High Power transmission line connections
1970
2020
2000
1990
1980
2010

## Slide 50: Miscellaneous
We had several troubles with usual suspects
  HV wiring
  High Power transmission line connections
1970
2020
2000
1990
1980
2010

## Slide 51: Improvements
All these troubles have been improved case by case and not occurred again
We simply need an experienced team
1970
2020
2000
1990
1980
2010

## Slide 52: Manpower strategy
Chart: Number of years of experience average
| 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
Number of year of experience average | 29.1111 | 30 | 29.4286 | 27.8 | 26 | 22.6667 | 18 | 17.75 | 14 | 10.2 | 8.2857 | 9.2857 | 10.2857 | 11.375 | 12.375 | 13.375
Stats | -1 | -1 | -1 | 0.59 | 0.61 | -1 | 0.83 | 0.45 | 1.8 | 1.41 | 1.1 | 0.81 | 0.48 | 0.3 | -1 | -1
Good Machine = (when my boss does not hear about it) =
(a*efficiency)*(b*reliability)*(c*AVAILABILITY)*(d*Experienced team)*k

## Slide 53: Manpower strategy
Availability of an Injector is the key parameter
CERN’s total annual electricity consumption is 1 TWh, for an operation of almost 7000 hours per year, 130 MW average
When SPS is down, almost 40 % of the electrical bill is for nothing (lost money)
  20 % for LHC cryogenics + cooling and ventilation
  10 % for LHC experiments
  7 % for the North Area experiments
  (http://cds.cern.ch/record/1324541?ln=en)
When SPS is down, electrical bill costs 5 000 CHF / hour
SPS RF is down ~ 1 % of the SPS operating time, 70 hours lost per year
Hiring a new colleague with three years overlap before retirement of an experienced colleague would save 1% additional along three years, 210 hours x 5000 CHF/hour = 1 MCHF !
1 % of the SPS operating time costs
~ 350,000 CHF per year (electrical bill only)
Please do hire young persons early enough
to ensure a correct overlap and experience sharing !

## Slide 54: Maintenance strategy
From 1970 to 2009, preventive maintenance was systematically done on the whole series of items, regardless the quantity in operation
Nowadays, we are not preparing large series of spares anymore, except few specific items such as trolleys or RF loads, we are ‘only’ having: ‘Two tested spares of everything everywhere’
We successfully modified the balance
preventive maintenance / corrective actions
Chart: Number of Staff
| 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
Staff | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 7 | 6 | 6 | 6 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
SPS RF Downtime % | -1 | -1 | -1 | 0.59 | 0.61 | -1 | 0.83 | 0.45 | 1.8 | 1.41 | 1.1 | 0.81 | 0.48 | 0.3 | -1 | -1

## Slide 55: Conclusion
We had several major failures along this long period of time, mostly ageing of components
  15-20 years for FPC
  20 years HVPS main items
  15 years controls
  30 years infrastructure
  Not any major RF amplifier trouble, tubes are very nice devices
A good balance of preventive maintenance / corrective actions allows good results, if and only if
  Systems have correctly been overdesigned (redundancy)
  Systems are as simple as possible (minimum number of items, of connections, of interlocks, …)
  Team has enough experienced staff
1970
2020
2000
1990
1980
2010

## Slide 56
Thank you very much for your attention
I wish you all to never experience that !