## Slide 1: IDE DCS development overview
Ewa Stanecka, ID Week, CERN 29.10.2013

## Slide 2: Overview
Actions in 2013
  Thermal enclosure heaters control system upgrade
  IDE DCS upgrade
  SR1 IDE DCS test system
Plans for 2014
  New systems integration
    Thermosiphon
    Sonar

## Slide 3: IDE DCS projects
ATLIDEEVCOOL
cooling plant
SCT & Pixel cooling
ATLIDEEVENV
ID environment monitoring
ATLIDETEH
thermal enclosure heater pads
ATLIDEMAG
magnetic field monitoring
ATLIDERAD
radiation monitoring
ATLIDEBLM
beam conditions
ATLAS network
IDE LCS:
overall FSM
beam monitoring
IDE racks monitoring
safety scripts
ATLIDEBCM
beam conditions
luminosity
ATLIDESNR
degassing
leak check
- mass flowmeter
New
Follow
Pixel
schedule

## Slide 4: TEH
TEH control replaced with new one:
  Mechanical improvements to card/backplane
  Improved remote control and interlock
May/June 2013 -> EC C and EC A is commissioned and tested
  each „heater pad group” was switched separately to check mapping
  All left for ~ 30min in „auto” mode
  Very smooth start for heater pads that were working during normal detector operation
  Software/hardware mapping verified and corrected for pads that were not in use so far
August 2013 –> Consolidation of TEH pads/sensor connections on PP1 side C, recovered 15 out of 17 bad pad/sensor connections.
  Need to implement recovered channels into TEH DCS configuration
Tuning PID parameters for operation – to be done with cooling operational

## Slide 5: DCS upgrade
IDE DCS follows ATLAS DCS LS1 upgrade plan, that includes important changes both in hardware and in software:
  New computers DELL PowerEdge R610
    installed 6 new machines in P1, old machines kept until new system commissioning
  OS system upgrade: Windows NT to Linux
  PVSS-> WinCC 3.11
  CAN bus interfaces: KVASER->Systec
  OPC DA server -> OPC UA server
We plan to finish upgrade of IDE DCS before end of 2013
Concern: we have non standard parts (e.g. ELMBs) in IDE, need to test carefully

## Slide 6: IDE DCS test system in SR1
Task | Status
TEH crate installation | done
OS system, WinCC + OPC UA installation | done
Systec box stand alone test | done
Systec box test with TEH hardware | November 2013
Script for config file for the new OPC UA | November 2013
Full system tests | November 2013
System test for TEH system installed crate installed
To test full DCS upgrade procedure for TEH system, which uses non-standard ELMBs.

## Slide 7: New systems integration
Thermosiphon
  Prepare panels for monitoring thermosiphon
    detector parts remain unchanged, the same control on single line level
    monitoring of the plant changes
      Thermosiphon will be monitored from the local server based on UNICOS CPC 6 framework of EN/ICE
      These local data servers will be located in CCC
      ID DCS and Thermosiphon data exchange via DIP (?)
      A few crucial parameters will be monitored directly from PLC
    Work to be done in IDE DCS
      Exercise communication with CCC and PLC
      define list of parameters to be exchanged and operation procedures
      replace “compressor module” by “thermosiphon module”, panels etc.
Sonar – will be integrated in IDE DCS for the first time. Still some development needed in particular implementation of Final Machine State. For more details see Greg’s talk.

## Slide 8: Plans for 2014
Early 2014 – integration of Sonar project into IDE and ATLAS FSM
Adjust mapping of environmental sensors in DCS configurations
Prepare for operation with cooling in summer 2014
Optimization, consolidation, code clean-up on going throughout LS1
Very detailed list of tasks can be consulted here: https://twiki.cern.ch/twiki/bin/viewauth/Atlas/IDDcsTasksLS1

## Slide 9: Summary
IDE DCS focuses now to finish upgrade by the end of 2013
Integrate new systems thermosiphon and sonar early 2014
TEH tuning with cooling start-up in summer 2014
Continuous efforts on system consolidation and improvements