## Slide 1: Control System Considerations for ADS
EuCARD-2/MAX Accelerators for Accelerator Driven Systems Workshop, CERN, March 20-21, 2014
Klemen Žagar <klemen.zagar@cosylab.com>
Robert Modic <robert.modic@cosylab.com>
Mark Pleško <mark.plesko@cosylab.com>

## Slide 2: High Availability
Fault tolerance and redundancy of the accelerator
  use of components far from their limits,
  parallel and serial redundancy of components,
  ability to repair failing section.
Control strategies for high availability
  Reliable components in the first place
  Redundant elements
  Protection systems without false positives
  Predicting faults before they occur
  Working around faulty equipment

## Slide 3: Standard CS Architecture

## Slide 4: Planning: work breakdown

## Slide 5: Hardware platform
Considerations:
  Maturity
  Performance
  Use in other facilities
  Obsolescence management
Today’s choices:
  VME [mature, nearing obsolescence]
  cPCI [suboptimal performance; cPCIe immature]
  PXI, PXIe [limited choice of vendors]
  mTCA/ATCA, mTCA.4 for physics [not much support from industry – yet]

## Slide 6: Software Framework
We recommend EPICS as the control system infrastructure.
  Widely used in ACC community.
  Good community and commercial support.
  Significant reuse of existing components possible.
  Mature and proven technology.
  Hooks allow implementation of a redundancy scheme.

## Slide 7: About EPICS
Thermo- meter
Computer Interface
Computer Interface
Computer Interface
Channel Access Server
(IOC)
Process Variables:
CWS-PHTS-DLHT:VC1-FCVZ
Channel Access Client
Channel Access Client
Flow Control Valve
Sub-system
CWS-PHTS-DLHT:VC1-FCVY1
CWS-PHTS-DLHT:VC1-FCVY2
CWS-PHTS-DLHT:MT2-TT

## Slide 8: EPICS Data Flow
The Channel Access network communication protocol.
  UDP for discovery.
  TCP for data exchange.
CA Server
CA Client
Channel Access Client
Who has a PV named “CWS-PHTS-DLHT:TTSPTARGET”?
I do.
What is its value?
25.5 degC
Change its value to 30.5
“connection request” or “search request”
OK, it is now 30.5
Notify me when the value changes
It is now 20.5 degC
It is now 10.3 degC
It is now 9.2 degC
“put” or
“caPut”
“get” or
“caGet”
“set a monitor”
“post an event”
or
“post a monitor”
“put complete”
Process Variables:
Channel Access Server
CWS-PHTS-DLHT:VC1-FCVZ
CWS-PHTS-DLHT:VC1-FCVY1
CWS-PHTS-DLHT:VC1-FCVY2
CWS-PHTS-DLHT:TTSPTARGET

## Slide 9: EPICS and redundancy
One of the IOCs is a primary, and one is a backup.
Primary IOC sends all state changes (e.g., changes of values) to the backup to keep it in sync.
if heartbeat fails, backup node takes over, in the same state where the primary left off.

## Slide 10: Equipment interfaces
How to integrate equipment:
Redundancy?

## Slide 11: Use And Integration Of PLCs
Logic neither complex nor very fast (>10ms)  robust.
Used in off-the-shelf industrial systems
  Cryo plant, vacuum, building automation/HVAC, …
Used for personnel protection (interlocks).

## Slide 12: Industrial Redundant Systems
PLCs
  implement redundancy in the CPU and with redundant hot swappable IO modules.
Network switches
  Predefining routing tables on nodes and switches
  This way communication can resume more quickly after switchover

## Slide 13: Machine protection system
Multiple levels of protection:
  Hardwired protection system. Required for nuclear safety.
  Personnel protection system.
  Machine/investment protection. Quick reaction to faults. Graceful shutdown.
The first two are outside the scope of control system.
  But can be integrated with it (e.g., via 4-20mA signal interface).
  MPS issues a mitigation action when a problem is detected.
Topology:

## Slide 14: Machine Protection is Redundant to Control System

## Slide 15: Machine protection system

## Slide 16: Predictive diagnostics
Statistical analysis of archived data (e.g., trends) to identify components nearing a fault.
Model and detailed monitoring of subsystems.
  E.g., monitoring of vibrations in mechanical subsystems.
Uses:
  Preventive maintenance planning.
  Preventively taking a component off-line.

## Slide 17: Virtual accelerator
Simulator of the machine.
Uses real-time configuration data of beamline elements to simulate beam characteristics.
Useful to analyze failure scenarios.
An R&D topic: automatic reconfiguration in case of a subsystem failure.

## Slide 18: Key recommendations
Initiate collaboration on control system with similar projects.
Introduce a naming convention early in the project.
Standardize and define control system interfaces for all delivered components and devices at the time of procurement.
Equip RFQ@UCL with fully functional and stable control system for its operation.
Foresee time and resources for reliability and availability investigation on RFQ@UCL.
Define the scope of the control system well – if subsystems don’t have a control system, foresee that it needs to be developed.

## Slide 19: Questions

## Slide 20: Alarms
Supervision of alarm state.
Guides operator in reacting to alarms.
E.g., BEAST.
  Part of the Control System Studio suite.

## Slide 21: Archiving
Storing values of process variables (PVs) through time.
Usage:
  Monitoring (and analysis) of (mid-/long-)term trends.
  Predictive diagnostics.
  Comparison of performance at various times.
E.g., BEAUTY.
  Part of Control System Studio.
Not a high-performance scientific archiving tool!

## Slide 22: Timing system

## Slide 23: Equipment interfaces
The Control Box

## Slide 24: ITER CODAC
Packaging of control system software.
  Operating system.
  EPICS.
  User interface tools.
In addition, ITER-specific tools
  E.g., Self Description Data toolkit for providing meta-data and development of “plant system instrumentation & control”.
Can be used elsewhere as a baseline
  E.g., ESS.