## Slide 1: CO2 Detector cooling
L. Zwalinski, P. Tropea
PH-DT-DI

## Slide 2: CO2 Detector cooling training
Why and how?
Some history on detector cooling
From present to future LHC experiments
Current trends and future developments Evaporative cooling: thermo siphon or CO2 pumped cycle
Design a system for its whole lifetime Redundancy, maintainability
How will the system be operated? Cooling/detector interface, operation, long term monitoring
Start!
What people do?
And be happy for the rest of life!
I am curious!
Let’s work!
I need some cooling for my detector, guidelines? What counts and what is negligible

## Slide 3: Detector cooling: why?
Dissipate the heat produced by:
  detector
  electronics
  cables
…many different reasons!
3 Half Disks
Port Cards and POH
DC-DC converters
Cooling tubes
and Cables
CO2 cooling tubes
and flex cables
K. Arndt, CMS Phase I Pixel detector EDR (https://indico.cern.ch/event/278220/)
Maintain a neutral environment between different detectors: active thermal screens
DT
Cold side
Warm side
Passive insulation
Heater
Cold plate
P. Petagna, Thermal enclosures & environmental management, 2008
Guarantee detector lifetime
  Silicon detectors
  Avoid thermal runaway
  Avoid reversed annealing
  Tsilicon < -5ºC

## Slide 4: Detector cooling: what?
Some naming and geography for a complex system
Cooling plant
Manifold
Main pipework
Detector transfer lines
Detector distribution
manifold
Detector
& on board
cooling loops
THIS IS NOT A TRIVIAL FRIDGE!

## Slide 5: Cooling of LHC experiments – “room” T
Alice
SPD 2 phase C4F10 15 °C
HMPID, SSD & SDD, TPC, TRD, TOF & Calorimeters
Water 16-18 °C
Water, C4F10, C6F14
CMS
Muons, ECAL & HCAL calorimeters, Diffusion pumps & magnet Busbar
Demineralized water 16-18 °C
Racks, PC farm
Tap water
16-18 °C
ATLAS
Muons, LAr & Tile Calorimeters, Diffusion Pumps, Rod Racks Demineralized or “treated” water 15-20 °C
TRT, CABLES
Liquid C6F14 15-20 °C
LHCb
RICH1&2 Liquid C6F14 10 °C
Calorimeters, OT, Muons, Racks
Water 16-18 °C
Pretty well known technologies, still very challenging for the application!
Magnetic field, radiation, etc.
24/7 operation, reduced accessibility
No space/no time/no mass requirements

## Slide 6: Cooling of LHC experiments – Low T
C6F14, CO2, C3F8
Alice
PHOS crystals
Liquid C6F14
-25 °C
CMS
Tracker, Pixel, Preshower, Tracker/ECAL active thermal screen
Liquid C6F14
-25 °C
ATLAS
Silicon detectors
Evaporative C3F8 -25°C
LHCb
VELO
Evaporative CO2 -25 °C
Introducing further difficulties:
Environmental management
Insulation
Let’s see few examples!

## Slide 7: Detector cooling, low T - liquid
Typical system layout
CMS Tracker, Pixel , PreshoweR, 7 plants, 220 loops, 150 kW, -25C
P. Tropea, The CMS Tracker Fluorocarbon Cooling System , CERN Engineering Forum: Experiences from LHC cooling systems, 30 October 2008

## Slide 8: Detector cooling: low T - evaporative
Sketch from:
M. Battistin (EN/CV-DC), ATLAS ID Evaporative Cooling System
ATLAS ID review
20 September 2007
Sketch from:
M. Battistin (EN/CV-DC), ATLAS ID Evaporative Cooling System
ATLAS ID review
20 September 2007
Typical system layout
M. Battistin (EN/CV-DC), ATLAS ID Evaporative Cooling System
ATLAS ID review, 20 September 2007
ATLAS Pixel & SCT: 204 loops, 60 kW, -25C

## Slide 9: What is next for low T?
Evaporative cooling vs liquid cooling
Evaporative cooling: WOW!
Low flow for higher Heat Transfer Coefficient (latent heat of evaporation adds to convection): smaller pipes
Limited temperature excursion on the detector (isothermal evaporation)
Temperature control through pressure control
But…
More complex system: evaporators on-detector and process design tightly linked!
Flow distribution
Dry out
EXPERTS NEEDED!

## Slide 10: Thermosiphon system
Surface:
Condenser
Water circuit
Low T chiller
Brine circuit
Surface-underground
C3F8 piping
Underground
USA15 by-pass unit
Connection to existing ID evaporative cooling system
ATLAS Surface
USA15
PX15
UX15
Pictures from: M. Battistin & all TS team ATLAS ID Week CERN October 2013
ATLAS Pix & SCT
EN/CV & PH-DT

## Slide 11: Thermosiphon system
Why thermosiphon solution:
No active components
Leaks reduction (caused by compressors vibrations)
Possibility to decrease evaporation temperature from -20 °C to -25°C and to -30°C using blends C3F8-C2F6
PR
thermal
screen
others
4 liquid lines
4 gas lines
liquid
tank
pneumatic
valve
manual
valve
manual
valve
dummy
load
BPR
pixel
6 X SCT
manual
valve
pneumatic
valve
UX15
USA15
underground
surface
7 Haug
compressors
Heater
dummy
load
Heater
condenser
liquid
tank
Sub-cooler
THERMOSIPHON
EVAPORATIVE
Chiller

## Slide 12: Thermosiphon system

## Slide 13: Evaporative CO2 in pumping cycle
Significant saving of cooling hardware (material budget) into the detector due to the physical properties:
large latent heat of evaporation
low liquid viscosity
high heat transfer coefficient
high thermal stability due to the high pressure
Very practical fluid to work (environmental friendly, not activated)
Practical range of the detector application -450C to +250C
What is different?
Pictures from: L.Zwalinski et al. THE CONTROL SYSTEM FOR THE CO2 COOLING PLANTS FOR PHYSICS EXPERIMENTS, ICALEPCS 2013, San Francisco CA

## Slide 14: CO2 2PACL systems by PH-DT
system family
Experiment | Project name | PLC/DAQ Brand | Project status | Cooling power
ATLAS | SR1 | Siemens | Completed | 2kW
 | IBL | Schneider | Under development | 2x3.3kW
CMS | TIF | Schneider | Completed | 15kW
 | Pixel phase 1 | Schneider | Under development | 2x15kW
General purpose ATLAS & CMS | CORA | Siemens | Completed | 2kW
ATLAS & Belle | MARCO | Siemens | Completed | 1kW
ATLAS & CMS & LHCb ILC-PPC founded by AIDA project | TRACI | Siemens NI LabVIEW DAQ | Completed | 100W
Picture from: B.Verlaat CO2 cooling is getting hot in high-energy physics CERN COURIER May 2012

## Slide 15: CO2 2PACL systems by PH-DT
ATLAS IBL
Plants @ USA15 level 3
Collaboration with Nikhef and EN/CV/DC

## Slide 16: CO2 2PACL systems by PH-DT
ATLAS IBL
2x3.3kW cooling power
2x plant cores, 2x chillers, 1x accumulator and controls placed in USA15
Transfer line connecting USA15 with UX15 ~100m long
Manifold and Junction box inside the toroid area
CO2 distribution via flexible vacuum insulated lines up to the dry volume
Vacuum system in UX15
Pictures from: B.Verlaat EDMS1233482

## Slide 17: CO2 2PACL systems by PH-DT
New Pixel detector for CMS to arrive in 2016
15 kW total cooling power @ -20°C
One full scale mock up of the system ready in 2013 @ TIF
Full cooling system at P5 end of 2014
CMS TIF (test facility for Pix upgrade)
125 M silicon pixels (x2 compared to present detector)
  4 Barrel layers
  3 Forward discs on each side

## Slide 18: CO2 2PACL systems by PH-DT
Biggest system ever built on 2 PACL principle
Fully built in PH-DT workshop (THANKS!)
Controls in PVSS, merging of PH-DT gas and cooling expertise (GREAT!)
CMS Pixel Phase I upgrade
Picture from: S. Pavis, PVSS controls for CMS Pixel Phase I Upgrade

## Slide 19: Where did we start from?
The road we followed and we’d like to follow in the future
For CO2 evaporative cooling system design (and not only):
MULTIDISCIPLINARY APPROACH
Just to begin with….
Thermal contact & thermal needs
Power dissipation
Simulations

## Slide 20: Thermal load
I need some cooling for…
Cooling plant
Transfer line
CMS-Upg. -Inner Barrel Aleksis Chávez Niemelä,
Detector heat
Thermal / Mechanical structure (Conductance)
Evaporative Heat Transfer (Conductance)
Cooling tube distribution (Pressure drop*)
Cooling transfer line (Pressure drop*)
* Pressure drop in a 2-phase system changes the boiling pressure and is manifested as a temperature drop. Needs therefore to be accounted for in the design of the overall thermal chain together with the conductance in the structure.
Detector
Cooling lines
Heat transfer
Heat transfer
Conductance
Pressure drop
Is your load:
Stable / changing over the day
Fix/increasing along the years
Uniform
Detector experts & cooling engineers!

## Slide 21: my thermal contact could look like…
Thus the coolant temperature…
Pictures from:
M. Olcese, Mechanics and cooling of pixel detectors, NIM A 465 (2001)
(CFRP) Mechanical support
Metallic pipe
Thermal conductive ledge
(Kapton, flex…)
Sensor
R/O chips
Critical thermal contact!
(DCTE, surface of contact…)
With this thermal contact/detector layout:
What is the ΔT between coolant and your critical parts of the detector?
How do your pipes look like? (length, diameter)
Thermodynamic & detector experts!

## Slide 22: Let’s start seeing if it could work
CoBra calculator (J. Noite, B. Verlaat) developed to predict flow regime and fluid properties changes (DT and DP) along the pipes (Prof. Thome model for 2-phase).
Simulation & mock-ups for evaporative cooling design
Electronics
Detector Inlet
Detector
Detector Outlet
Pictures from: J. Noite, CMS Bpix cooling loop simulation
Have you tested your model?
Thermodynamic experts!

## Slide 23: By the way: the detector should also…
…operate in a very different temperature range
J. Noite: HTC comparison at -20°C and +15°C
Checkout & commissioning conditions: no insulation/drying available
Room T operation? With evaporative system, a consistently different Heat Transfer Coefficient is to be expected !
Thermodynamic & detector experts!

## Slide 24: Ok…and now?
Thermal contact & thermal needs
Power dissipation
Simulations
Cooling system design process
The basics detector needs
Now we should start looking at:
Which environment?
How do I connect the parts of the system?
How reliable do I need my system to be?

## Slide 25: Which environment?
Experimental caverns
100 m underground
Ionizing radiation
Magnetic field
And how to decide the geography….
Service caverns
80 m underground
Accessible during LHC operation
No radiation nor magnetic field
Ideally:
Access active components 24/7
No issues of magnetic field and/or radiation for the selection of parts
i.e.: place as much as possible of your system in Service caverns…..but
Radiation protection simulations are needed, to prove everyone is safe when working around the system!
DO NOT FORGET ANCILLARY SERVICES! (dry air, power, water, etc.)
Designers & safety experts!

## Slide 26: How do we bring coolant to the detector?
2PACL CO2 systems:
inlet to the detector shall be liquid, subcooled
Low operating T: suffering from ambient heat, insulation!
Concentric transfer lines allow perfect heat exchange between inlet and outlet
Granularity (size of detector manifolds) determines Δp at the detector inlet, guides the sizing of the transfer lines & the selection of your pump!!
….speaking about transfer lines and granularity
Outlet manifold: Pressure = fixed
Inlet manifold: Temperature = fixed
Tliquid
T2phase
Inlet liquid
Vapor return
Pipe length
Plant
Detector
Transfer line
Pictures from: B. Verlaat, Forum on Tracking Detector Mechanics, 2013
Ambient heat
Cooling, integration, detector experts!

## Slide 27: Ok, we have a baseline
How will my system look like?
Picture from: A. D’Auria, Process and Instrumentation diagram for CMS Pixel CO2 cooling system
P&I (process and instrumentation)
Component selection
3D modeling for construction and integration with detector integration office!
Membrane pump
150 g/s liquid CO2
-40 to +15°C operating T
157 bar testing p
Remote head
Frequency driver
Remote stroke adjustment
Design, control, mechanics, process experts!

## Slide 28: The layout is there: how do I build it?
QA matters
During construction
CO2 systems design pressure above 100 bar
QA for the construction shall be tight: and be the same over all the system (plant to detector!)
samples for welds, in order to establish accurate welding procedure
Visual inspections by experts, x-rays on sampling welds
P tests following EU standards
Leak tests
Careful choice of connectors!
Integration!
Welding, mechanics, safety and integration experts!

## Slide 29: But we also need to know….
Operation scenarios
  IBL: Operation, Stand-by, Bake-out!
  What is the availability rate needed?
    IBL: Run always!
    What are foreseen maintenance time slots available?
  What happens if cooling gets off?
  Apply alarms philosophy adopted to your needs.
Detector interface
  Who drives the cooling system?
  Who and how decides on the cooling system settings?
  What are the interlocks and the consequences?
  When and how cooling should be stopped?
  Who and how reads the data from the cooling system?
At least very simple
risk analysis is needed!
Detector, cooling and control experts!

## Slide 30: Long live the king!
Redundancy
  Mechanics
    Completely independent systems or shared components/modules
    Use redundant sensors for the key operations
  Control
    One PLC vs multi PLCs system
    One central SCADA server or many individual ones
    Distributed IOs or PLC IOs
    Fieldbus or direct connections and what architecture
  Electrical power
    Normal power, UPS or diesels
    Single or at least two different power sources
Adapt your choice to the detector needs!
ATLAS IBL
shared & modular architecture
Picture from: O.Crespo-Lopez ,L.Zwalinski EDMS1331128

## Slide 31: Long live the king!
Maintainability
  Modularity
  Accessibility
  Clear procedures
Plant Core Front
Plant Core Back
Access to all warm mechanical components from the outside
Easy to take off foam box front cover providing access to all cold components
Control components and connections kept outside
Quick pump dismounting with lifting tool
Chiller
Plant Core
Manifold outside
Manifold inside
Access to all warm mechanical components from the outside
All cold components installed inside fridge box with like cabinet doors opening
Control components and connections kept outside
In case of catastrophic failure we can replace one single module.
It provides more flexibility in operation.
Much easier installation especially in the underground areas.
Quick and easy maintenance.
Decreases the need of using special equipment.
Decrease significantly the number of human errors.
Increase safety of the maintenance team.

## Slide 32: …and they lived happily ever after
Detector interface
  What are the interactions foreseen between detector and cooling system? One way or two way communication?
  Detector Control System: DIP or/and direct communication with PLC.
  Detector Safety System: hard wired signals
  Well defined key information to the detector (*not too much but also don’t limit it to on/off state as people will ask for more)
Pictures from: L.Zwalinski et al. The control system for the CO2 cooling plants for physics experiments, ICALEPCS 2013, San Francisco CA

## Slide 33: …and they lived happily ever after
Operation
  Understandable interfaces with same philosophy and operation interactions for all new detector cooling systems.
  Clear and intuitive navigation.
  Easy access inside and outside CERN for the experts and support team.
  Access control with different privileges levels driven by e-groups.
  Diagnostic expert interface panels.
Our selected solution is
UNICOS CPC6
& WinCC OA
Pictures from: M.Ostrega, M.Zimny, L.Zwalinski ATLAS IBL CO2 cooling system
Control and detector experts!

## Slide 34: …and they lived happily ever after
Long term monitoring
  Detector data bases
  LHC Logging
  EN-ICE ORACLE
  Local DB
Remember to make your data safe and available
for any later analysis even after very long time!
Our current choice for most
of the applications is
LHC Logging
Control experts!

## Slide 35: Summary & outlook
The design of a cooling system must involve experts in many different fields:
  Detector design
  Mechanics and thermal contact
  Cooling process
  Safety (pressure & radiation protection)
  Controls
  Thermodynamics
  Welding
  Integration
  Detector operation
CO2 cooling system design is not trivial: keep it as simple as possible and make sure all parties are involved!
What have we learnt

## Slide 36: Detector cooling in PH-DT
STAG
form CUT
THANKS!!!

## Slide 37: Some references…
J. Godlewski, S. McMahon, A. Tauro, B. Verlaat, V. Vacek, P. Petagna, M. Battistin, Engineering forum: experiences from cooling systems for LHC detectors 2008
Workshop on quality issues in current and future silicon detectors, 2011
H. Postema, VERTEX 2011
B. Verlaat, ECFA High luminosity LHC Experiments Workshop, 2013
P. Petagna, VERTEX 2013
J. Daguin, CERN detector seminar 2013
Forum on Tracking Detector Mechanics, 2013
L. Zwalinski et al. The control system for the CO2 cooling plants for physics experiments, ICALEPCS 2013
And a big thank you to all people having given precious inputs!

## Slide 38: Backup slides

## Slide 39: Why CO2 in particle physics detectors?
Typical Silicon detectors requirements:
Distributed heat load up to 20 kW/m2
Low temperature operation to reduce radiation damage effects (down to -40˚C)
Room temperature for testing
Reliable cooling with minimal temperature gradients
Minimization of material inside the detector active volume
Current BPIX Services
h<2.2 : weight = 16.9 Kg (3 layer)
Upgraded BPIX Services
h<2.2 : weight = 6.5 Kg (4 layer)
Current 2 disk
Upgraded 3 disks
Radiation length
Current 3 layer
Upgraded 4 layer
Radiation length
Today: liquid C6F14
Low thermal capacity (≈1 KJ.Kg-1.K-1)
High density (≈1,7 kg.l-1)
“Big” pipes (3.0 mm ID / 0.3 mm thick)
Tomorrow: evaporative CO2
Enhanced thermal capacity (≈2 KJ.Kg-1.K-1)
Lower density (≈1.0 kg.l-1)
Much smaller pipes (1.6 mm ID / 0.05 mm thick)

## Slide 40: How to evaporate liquid CO2 in your detector?
Detector
Cooling plant
Warm transfer
Chiller
Liquid circulation
Cold transfer
2PACL method:
(LHCb)
Refrigeration method:
(Atlas)
Vapor compression system
Pumped liquid system, cooled externally
Heater
Compressor
Pump
Compressor
BP. Regulator
Liquid
Vapor
2-phase
Pressure
Enthalpy
Liquid
Vapor
2-phase
Pressure
Enthalpy
Cooling plant
Detector