## Slide 1: Update on the Hardware commissioning
Roberto Saban
Commissioning of the Technical Systems of the LHC
LEMIC April 29th , 2008

## Slide 2: Status of the LHC

## Slide 3: Consolidation
Connection of the inner triplet left of CMS
Other repair work which includes
  The consolidation of the interconnection cryostat
  Repair of a cryogenic line inside the bayonet heat exchanger
  The replacement of plug-in modules where RF fingers buckled following the warm up
Cool down expected to start after week 17

## Slide 4: Preparation for Cool down
Cool down starts in three weeks: W19

## Slide 5: The latest cool downs
2
4
3
5
6
Presently three sectors are below 2K
The helium inventory in the LHC is 75 t
6 weeks to cool down from 300 to 2K +
3 weeks for stabilization at 2K
Courtesy S.Claudet
Sector 56
Sector 78
Sector 81
Sector 67
Sector 23
Sector 34

## Slide 6: Sector 56 : successful test steps

## Slide 7: Sector 56
Open
Days
400 kV power cut
Easter
w-e
w-e
w-e
Very high efficiency, thanks to improved powering test procedures, automated sequences, good performance of the cryogenics.

## Slide 8: Sector 56 : status
60 A: 93 out of 94 circuits commissioned
at nominal current
80/120 A:
    ML6&LR5 - all circuits fully commissioned
    ARC – 54% of steps completed
    IT – circuits not commissioned
600 A: 35 over 39 ARC circuits fully commissioned
IT – 1 circuit over 7 already at nominal
IPD: RD2.R5 fully commissioned
IPQ’s: 9 over 12 fully commissioned
for the remaining 3, one test step is missing
Main circuits: RB commissioning completed
RQD/F powered at 7 kA
IT: powered at nominal current in the 2 PC’s
configuration









7 TeV equivalent
5.5 TeV equivalent

## Slide 9: Sector 56 : the first inner triplet
on Thursday April 24th 2008

## Slide 10: Dipole training quenches
First at 10.004 A / two magnets
Second 10.227 A