## Slide 2: Status report of CRG activities
June 27th, 2014
LS1 Committee (LSC)
L. Tavian TE-CRG

## Slide 3: Content
Update on:
  DFBA progress
  Major overhauling and maintenance
  R2E at P4
  Re-commissioning status
  Helium spilling test in S23

## Slide 4: DFBA splices consolidation: completed !
100% of splices consolidated, 100% of sleeves welded, 100% DFBAs reclosed (26 May)
Only beam vacuum valves and alignment remaining on 2 DFBAs.
11 DFBAs (sect. 6-7, 8-1, 1-2, 2-3, 5-6, 7R) pressure tested
DFBs
Other consolidations / maintenance on DFBs
All safety valves re-qualified.
DFBX CL controls: IP 1, 2, 5, 8 (all IPs installation completed)
Several consolidations ongoing (protections, etc.), to be completed by end of July.
2 DFBM with non-nominal behaviour (DFBMB.4R2, DFBMC.5R2) being investigated and consolidated
Active cooling of DFBMB 4R8 screen (11 June)

## Slide 5: C199 maintenance contract LS1 for cryogenic maintenance activities of LHC, ATLAS & CMS
About 90% of work completed
Overall activities ongoing as planned with minor adjustment not affecting the availability of installations for operation (N.B. July still critical but feasible)
Demounting a cold compressor
Cartridges of a HP coalescer in Pt2 of LHC

## Slide 6: Status of LHC, ATLAS & CMS cryoplants maintenance and major overhauling
About 94% of work completed
C199 90%, Compressors 100%, motors 90%

## Slide 7
R2E @ P4: new cold compressor electronics
All new systems (Drives and AMB controls) validated at maximum speed and reduced load.
Validation at full load to be done (CW40-42).

## Slide 8: Sector flushing & pressure tests
Sector | PT | Flushing | NC after pressure test on QRL
S12 | Done | In progress | 1 leak on Header C: opening of the interconnect from 7th of July
S23 | Done | CW27 | RAS
S34 | CW29 | CW32 | N/A
S45 | CW31 | CW33 | N/A
S56 | Done | CW28 | Under investigation
S67 | Done | Done | RAS
S78 | In progress | CW30 | N/A
S81 | Done | Done | 1 leak on Header D (sub-sector D): Accepted

## Slide 9: First sector cool-down (Sector 67)
Towards readiness for
the 1st CSCM test
Week-end slow-down
(LN2 logistics)
Nitrogen precooling

## Slide 10: Sector 67 temperature stability

## Slide 11: LHC and Detectors cool down, LN2 Planning 2014
About 10’000 tons
LHC_67
Launched for S81 and detectors, organized for 6 remaining LHC sectors
S81

## Slide 12: LHe deliveries and forecast 2014 (CERN wide)
Voluntary slow-down of deliveries to match our available capacity at that time
In order to have 1st LHe storage ready after maintenance
In order to have last LHe storage ready after maintenance AND 1st sector to be filled
Very smooth logistics so far, with 98% of external storage already back at CERN!

## Slide 13
QSCB
QURA
QUIC
QURC
QURC
Storage
QSRA
QSCC
QSCC
QSCA
QSCB
QURA
QUIA
QURC
QURC
Storage
QSRA
QSCC
QSCC
QSCA
Legend
LHC Cryogenic Distributlion Line (QRL)
Maintenance/consolidation
Pressure tested
Non conformity / problem
Cool down
Electrical Feed Box (DFBA)
Superconducting Link
P4
P2
P1.8
Surface
Cavern
Shaft
P5 - CMS
CB
DVB
Tunnel
Sector 2-3
CMS solenoid
LN2 storage
N2 CS
LAr St.
ATLAS Calor.
Storage
P1 - ATLAS
Argon
MR
SR
Sector 1-2
Sector 5-6
QUIB
QSRB
Sector 6-7
QSCA
QURA
QUIC
QURC
QURC
QSRB
QSCC
QSCC
QSCB
Sector 3-4
Sector 4-5
QSRA
QSRB
P6
QSCA
QURA
QUIC
QURC
QURC
QSRB
QSCC
QSCC
QSCB
Sector 7-8
Sector 8-1
QSRA
Storage
CS
P8
Helium
MCS
SCS
MCB
SCB
DVB
ATLAS Toroid
ATLAS Solenoid
N2CB
DVB
LHC
QSC_(A,B,C): Warm Compressor Station
QSR_(A,B): Surface 4.5 K Cold Box
QURA: Underground 4.5 Cold Box
QURC: 1.8 K Unit Cold Box
QUI_(A,B,C): Cryogenic Interconnection Box
Experiments (M,S,N2)_CS: Warm Compressor Station
(M,S,N2)_CB: Cold Box
MCS: Magnet Compressor Station
DVB: Distribution valve Box
Operational/ Cryostart
Cryo-tuning
Status of the Cryogenic Systems of LHC, ATLAS and CMS
Maintenance/consolidation finished
Date: 25 June 2014
A.P. TE-CRG
Cold standby (experiments)
Storage
Storage
Storage

## Slide 14: Helium spilling test in S23
m= ~100 g/s

## Slide 15: Conclusion
DFBA activities: SMACC activities completed. Reconfiguration in progress.
Site-maintenance and major-overhauling activity: 94 % of progress. Site maintenance at P4 on the critical path.
Re-comminssioning:
  Pressure tests according to the schedule: Some NC to be treated.
  Sector cool-down: S67 completed ready for CSCM tests. S81 Ready for cool-down.
  Fluid logistics (He and LN2) on tracks
  The summer will be hot (large activity load during holidays time)