## Slide 2: Specifications and available protection mechanisms of the Beam Screen Heater electronic card
TRIKOUPIS Nikolaos

## Slide 3: Content
Presentation: Specifications and available protection mechanisms, by Nikolaos
Power on-load, AC/DC modes
Protections mechanisms
Operating the card
Operation of sector 6-7
Presentation: Integration of the Electrical Heaters in the control system, by Enrique
Discussion:
AC/DC modes of operation
Automatic enabling
I/O error, temporary and full stops

## Slide 4: Power on-load
Specifications | Value
Modes of operation | DC or AC (Approx. 4 seconds for switching between modes)
DC power output | 0-30W, Linear voltage 0-55V
DC power feedback | Valid immediately (after 2 seconds)
AC power output | 0-200W, Pulse-Width-Modulation of AC over 10 sec
AC power feedback | Stable after 3τ ~ 36 sec. Updated every 10 seconds.
AC power measurement

## Slide 5: DC/AC mode of operation
DC mode of operation
Load: Connected
AC mode of operation
Load: Connected
DC/AC mode of operation
Load: Disconnected
AC/DC or DC/AC transitions last max 4.2 sec

## Slide 6: Protections
Channel disabled when: | Auto recovery | Comments
Crate power-ON | No | 
Reset | No | 
Overtemperature of the heater | No | Diagnostic error is stored until acknowledged by an “Enable” command
Communication loss for > 10 sec | No | Diagnostic error is stored until acknowledged by an “Enable” command
Channel “Disable” command | No | 
Channel “Disconnect” command | No | 
Card heatsink overtemperature | No | Diagnostic error is stored until acknowledged by an “Enable” command
Relays malfunction (on DC->AC or AC->DC transition) | No | Diagnostic error is stored until acknowledged by an “Enable” command
PCB card reference out of bounds | Yes | As long as error is present, no min/max time
PCB signal digitization malfunction | Yes | Minimum 5 seconds on error, then automatic reset attempt
PCB backpanel unstable setpoint | Yes | As long as error is present, no min/max time
PCB backpanel unstable address | Yes | As long as error is present, no min/max time
Thermocouple reference out of bounds | Yes | This protection is managed by CIET and not the card

## Slide 7: Overtemperature protection
Upper hard interlock (On EH card)
Lower hard interlock (On EH card)
Soft interlock (Instrument specialist)
The soft interlock is set by the instrument specialist through the communication card
  Soft interlock is currently set to 40°C.
The hard interlocks are set on the EH card by jumpers
The 3 protections trigger an “Overtemperature” protection.
Chart: Temperature in °C
Blue: ThC correct polarity
Red: ThC inverse polarity
Chart: Temperature in °C

## Slide 8: Operation of the EHBS card
Commands |  |  | Result
Channel Enable/Disable | Load Connect/Disconnect | Mode DC/AC | 
Enable | Connect | DC | Channel enabled, load connected to DC, delivering DC power
Disable | Connect | DC | Channel disabled, load connected to DC, no DC power
Enable | Disconnect | DC | Channel disabled, load disconnected to DC, no DC power
Disable | Disconnect | DC | Channel disabled, load disconnected to DC, no DC power
Enable | Connect | AC | Channel enabled, load connected to AC, delivering AC power
Disable | Connect | AC | Channel disabled, load connected to AC, no AC power
Enable | Disconnect | AC | Channel disabled, load disconnected to AC, no AC power
Disable | Disconnect | AC | Channel disabled, load disconnected to AC, no AC power
Enable | Connect | DC->AC or AC->DC | Channel enabled, mode transition, load connected to AC/DC
Disable | Connect | DC->AC or AC->DC | Channel disabled, mode transition, load connected to AC/DC
Enable or Disable | Disconnect | DC->AC or AC->DC | Channel disabled, relays do not move, relay error
Enable command: ‘0’ for 15 sec and then ‘1’ for 15 sec
Disable command: ‘1’ for 15 sec and then ‘0’ for 15 sec

## Slide 9: Power DC precision

## Slide 10: Power AC precision

## Slide 11: Power DC->AC transition

## Slide 12: Power setpoint of 25W

## Slide 13: Typical thermocouple reading

## Slide 14: LBARB_24R6_EH843

## Slide 15: Questions?