## Slide 2: Pt4-Pt1-Pt5 surface and underground space requirements
C. Collazos, P. Fessia, C. Magnier
With key inputs from (and many thanks to)
J.-P. Burnet,
R. Calaga, S. Claudet, K. Dahlerup-Petersen, B. Feral, G. Ferlin, E. Todesco

## Slide 3: Summary
Pt 4: installation of the cryo-plant for RF
Pt1 and Pt5
  Space requirement system by system
    Crab cavities
    Cryogenics
    Cold powering
  Arrangement concepts
  Analysis building by building point by point
    Crab building
    Cold powering building
    Point 5
    Point 1
  Option comparisons
Conclusions

## Slide 4: Remarks
Space requirements shall be taken with an error band of ± 25 % in particular
All civil engineering structure are concepts not yet discussed with the CE team (no feasibility, costs,… ). The work with them starts today
Crab cavities: information according to the RF study performed till now.
Cryogenics
  Based on the LHC know how, probably well defined but piping could affect space need
Cold powering
  Power converters can be optimised for equipment cost or for volume occupancy according to project requirement and cost driving term
  DFH: the volume is guessed on the base of present DFBA as no other information is presently available
  QDS and QEE: based on 1st guess.

## Slide 5: Point 4: Cryogenic power plant for RF
This topic will the subject of an extended presentation by C. Magnier in an upcoming HL-TC where the proposal will be described in details and submitted to approval. As results it shall become baseline and it will affect the way in which CRG team will prepare the tendering

## Slide 6
Point 4 : 3D overview
PZ45
SHM4
SH4
SX4
SZ4
SU4
SD4
PM45
US45
UJ46
UJ44
UX45
PX46
TX46

## Slide 7
Pt4 surface : top view
in yellow the concerned
area
SU4
SX4
SD4
PM45
SUH4
PX46
POINT 5
UJ46
UJ44
SZ4

## Slide 8
Cryogenics area
SUH4
PX46
SX4
EXISTING TECHNICAL GALLERY
NEW TECHNICAL GALLERY
PLACE TO BE DEFINED (1.8mx2m)
Halfen supports

## Slide 9
Underground installation of cold box:
New proposition in TX46
PX46
TX46
UJ46
RB46
RB44
UJ44
UX45”RF” side
PZ45
UX45 ”CRYO” side
- TX46 is an empty cavern
- We could use PX46 for the pipes
- TX46 is “closed” to existing cryogenic
installation

## Slide 10
Vertical installation volume
Installation volume
65 m2
Height 7.5 m

## Slide 11
Space reservation in PX46 for services
8 m2

## Slide 12
Handling volume
400mm
RUX45 shielding
7300x2100x475h
ACSGA on trailer

## Slide 13
SSS trailer handling for vertical solution
35 degrees/floor
350mm

## Slide 14: Point 4 summary
The proposed solution in Point 4
  Minimizes the surface civil engineering
  Reduces the lengths of the underground cryogenic piping respect previous proposals
  Provides installation zone for the cold box in the nearest possible position respect the LHC machine tunnel
  Still provides all the required volume needed for transport manipulation
  In principle could allow anticipation of activities before LS2 start (to be studied)

## Slide 15: Point 1 and Point 5: Cryogenic power plant, RF crab cavity infrastructures, cold powering

## Slide 16: Space requirement system by system

## Slide 17: Crab cavities

## Slide 18: Crab cavities
 | Requirement | Area | Baseline/Option
RF power (2×IP) | 2×[3×14] m | 2×42 m2 | Underground/surface
LLRF racks (2×IP) | 2×[(5.6+4.4+7)×3.8] m | 2×65 m2 | Underground/surface
LLRF central racks(1×IP) | 2×3.8 m | 8 m2 | Underground/surface
HVPS (2×IP) | 2×[4×16] m | 2×65 m2 | Surface
Remark
LLRF requires Electromagnetic shielding and it is radiation sensitive

## Slide 19: Cryogenics

## Slide 20
STOCKAGE HELIUM (warm & cold)
Surface building (SD) (30mx10m)
WARM COMPRESSOR
BUILDING
600m2
PIT
UNDERGROUND
CAVERN
Illustrations : Serge Claudet (CRG)
QPLB

## Slide 21: Cryogenics
Cryogenic system | Where |  | 
Warm compressor | Surface | Area | 700 m2
 |  | Crane | 20 t
 |  | Type | Noise insulated
Surface SD building | Surface | Area | 30×10=300 m2
 |  | Crane | 5 t
Cold Compressor | Underground | Volume | 200 m3
 |  | Surface | 0 m2
 |  | Crane | 2 t
Remark
The electronics for the magnetic bearings of the cold compressor is radiation sensitive and maximum distance from its control electronics to the compressor is
50 m

## Slide 22: Cold powering

## Slide 23: Cold powering Circuits Q1 to D1
Q1 to D1 (for each IP side) |  |  |  |  |  | 
circuits connected to the DFHX |  |  |  |  |  | 
C.M. | Circuit / magnet | Op. current [kA] | PC current rating [kA] | N of circuits | N. of 19” racks /PC | Total racks/ Circuit type
Q1-Q3 | MQXF | 17.5 | 20 | 1 | 10 | 10
 | trim MQXF Q3 | ±2 | ±3.2 | 1 | 3 | 3
Q2A-Q2B | MQXF | 17.5 | 20 | 1 | 10 | 10
 | trim MQXF Q2 | ±0.3 | ±0.8 | 1 | 0.5 | 0.5
 | MCBXB | ±2.5 | ±3.2 | 4 | 3 | 12
CP | MCBXA | ±2.5 | ±3.2 | 2 | 3 | 6
 | MQSXF | ±0.182 | ±0.2 | 1 | 0.5 | 0.5
 | MCTXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
 | MCTSXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
 | MCDXF | ±0.193 | ±0.2 | 1 | 0.5 | 0.5
 | MCDSXF | ±0.193 | ±0.2 | 1 | 0.5 | 0.5
 | MCOXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
 | MCOSXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
 | MCSXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
 | MCSSXF | ±0.17-0.2 | ±0.2 | 1 | 0.5 | 0.5
D1 | MBXF | 11.8 | 16 | 1 | 9 | 9
Space needed | 
circuits connected to the DFHX | 
Total racks | 55
Installation surface [m2] | 40
Access/manipulation surface [m2] | 43
Linear installation extension [m] | 35
Height [m] | 2.6
Installation volume [m3] | 100
Cooling water flow rate [l/min] | 305

## Slide 24: Cold powering Circuits D2 to Q6
D2 to Q6 (for each IP side) |  |  |  |  |  | 
Circuits connected to the DFHM |  |  |  |  |  | 
C.M. | Circuit / magnet | Op. current [kA] | PC current rating [kA] | N. of circuits | N. of 19” racks /PC | Total/ circuit type
D2 | MBRD | 12.4 | 16 | 1 | 9 | 9
 | MCBRD | ±3 | ±4 | 4 | 4 | 16
Q4 | MQYY | 16.1 | 20 | 2 | 10 | 20
 | MCBYY | ±3 | ±4 | 4 | 4 | 16
Q5 | MCBY | 0.088 | ±0.12 | 6 | 0.25 | 1.5
 | MQY | 4.2 | 8 | 2 | 4 | 8
Q6 | MCBC | 0.1 | ±0.12 | 2 | 0.25 | 0.5
 | MQML | 5.39 | 8 | 2 | 4 | 8
Space needed | 
Circuits connected to the DFHM | 
Total racks | 79
Installation surface [m2] | 56
Access/manipulation surface [m2] | 60
Linear installation extension [m] | 50
Height [m] | 2.6
Installation volume [m3] | 145
Cooling water flow rate [l/min] | 400

## Slide 25: Cold powering arc
Continuous cryostat presently fed from DFBA (for each IP side) |  |  |  | 
Circuits connected to the DFHA |  |  |  | 
Magnet | PC current rating [kA] | N. of circuits | N. of 19” racks /PC | Total/ circuit type
MQT | ±0.6 | 2 | 0.5 | 1
MQS | ±0.6 | 2 | 0.5 | 1
MQTL | ±0.6 | 2 | 0.5 | 1
MQT | ±0.6 | 2 | 0.5 | 1
MSS | ±0.6 | 2 | 0.5 | 1
MO | ±0.6 | 4 | 0.5 | 2
MQM | 6 | 4 | 4 | 16
MQML | 6 | 4 | 4 | 16
D11 T trim | ±0.6 | 2 | 0.5 | 1
Space needed | 
Circuits connected to the DFHA | 
Total racks | 38
Installation surface [m2] | 27
Access/manipulation surface [m2] | 29
Linear installation extension [m] | 25
Height [m] | 2.6
Installation volume [m3] | 68
Cooling water flow rate [l/min] | NA
Space becoming free in RR by DFHM related PC | 
Racks removed | 34
Installation surface made available | 24
Linear installation extension [m] | 22

## Slide 26: Spare Power Converters
Cont. cryostat (for each IP side) |  |  | 
“DFHA” |  |  | 
N. spare | PC current rating [kA] | N. Circuit served | N. of 19” racks
Total 5 racks |  |  | 
Q1 to D1 (for each IP side) |  |  | 
“DFHX” |  |  | 
N. spare | PC current rating [kA] | N. Circuit served | N. of 19” racks
1 | 20 | 2 | 10
1 | 16 | 1 | 9
1 | ±3.2 | 7 | 3
1 | ±0.8 | 1 | 0.5
1 | 0.4 | 10 | 0.5
D2 to Q6 (for each IP side) |  |  | 
“DFHM” |  |  | 
N. spare | PC current rating [kA] | N. Circuit served | N. of 19” racks
1 | 20 | 2 | 10
1 | 8 | 4 | 3
1 | ±4 | 4 | 0.5
1 | ±0.12 | 8 | 0.5
Q1 to Q6 (for each IP side) |  |  | 
DFHX+ DFHM spares |  |  | 
N. spare | PC current rating [kA] | N. Circuit served | N. of 19” racks
1 | 20 | 5 | 10
1 | 8 | 4 | 3
1 | ±4 | 12 | 0.5
1 | 0.4 | 10 | 0.5
1 | ±0.12 | 8 | 0.25
Q1 to Q6 (for each IP side) | 
DFHX+ DFHM spares | 
Installation surface [m2] | 10
Access/manipulation surface [m2] | 12
Linear installation extension [m] | 9
Height [m] | 2.6
Installation volume [m3] | 18
Cooling water flow rate [l/min] | 100

## Slide 27: Quench detection, Q.H. powering
Q1 to D1 (for each IP side) |  |  |  | 
circuits connected to the DFHX |  |  |  | 
C.M. | Circuit | DQS | Q.H. | Total racks
Q1-Q3 | MQXF | 1 | 2 | 1.5
 | trim MQXF Q3 | 1 | NA | 0.5
Q2A-Q2B | MQXF | 1 | 2 | 1.5
 | trim MQXF Q2 | 1 | NA | 0.5
 | MCBXB | 4 | Not def | 2
CP | MCBXA | 2 | 1 | 1.5
 | MQSXF | 1 | 0 | 0.5
 | MCTXF | 1 | 0 | 0.5
 | MCTSXF | 1 | 0 | 0.5
 | MCDXF | 1 | 0 | 0.5
 | MCDSXF | 1 | 0 | 0.5
 | MCOXF | 1 | 0 | 0.5
 | MCOSXF | 1 | 0 | 0.5
 | MCSXF | 1 | 0 | 0.5
 | MCSSXF | 1 | 0 | 0.5
D1 | MBXF | 1 | 1* | 0.5
D2 to Q6 (for each IP side) |  |  |  | 
Circuits connected to the DFHM |  |  |  | 
C.M. | Magnet | DQS | Q.H. | Total racks
D2 | MBRD | 1 | 1* | 1
 | MCBRD | 4 | Not def | 2
Q4 | MQYY | 2 | 1* | 1.5
 | MCBYY | 4 | Not def | 2
Q5 | MCBY | 6 | 0 | 3
 | MQY | 2 | 1 | 1
Q6 | MCBC | 2 | 0 | 1
 | MQML | 2 | 1 | 1
Space needed SC link included |  | 
 | DFHX related | DFHM related
Total racks | 14 | 14
Installation surface [m2] | 9 | 9
Access/manipulation surface [m2] | 11 | 11
Linear installation extension [m] | 9 | 9
Height [m] | 1.8 | 1.8
Installation volume [m3] | 25 | 25
Plus 0.5 rack for each SC link itself
*
Present design does not feature Q.H.

## Slide 28: Quench extraction
Quench extraction system main equipment modules |  | 
Equipment | Dimensions [m] | remark
Energy extraction switch | 2×2×2 [L×W×H] | Solid state based switches best guess for dimension 20 kA
Dump resistor | 1×1×1 [L×W×H] | Cooled dump resistor with water to coolant heat exchanger. Best guess dimension for 10 MJ
Quench extraction number and volume approximation |  | 
Equipment | No of units | Volume best guess on the base of energies and current
Energy extraction switch | 5 | 2×[2×2×2]+3×[2×2×1]
Dump resistor | 7 | 4×[1×1×1]+3×[0.5×0.5×0.5]
Quench extraction 1st guess installation surface and volume |  | 
Equipment | Surface including access [m2] | Volume [m3]
Energy extraction switch | 42 | 30
Dump resistor | 20 | 5

## Slide 29: Cold Powering volume and surface total needs
Q1 to D1 (for each IP side) including DFHX and DFHM |  |  |  |  |  | 
 | Q1 to D1 | D2 to Q6 | Spare PC Q1 to Q6 | QDS | QEE | total
Installation surface [m2] | 52 | 68 | 10 | 18 | 25 | 173
Access/manipulation surface [m2] | 56 | 73 | 12 | 22 | 37 | 200
Linear installation extension [m] | 46 | 61 | 9 | 18 | 14 | 148
Installation volume [m3] | 120 | 164 | 18 | 50 | 35 | 387
Cooling water flow rate [l/min] | 305 | 400 | 100 | NA | NA | 810
DFH (X M A) | 
Length [m] | 11
Width [m] | 0.95
Height [m] | 1800
Installation surface [m2] | 11
Access surface [m2] | 13
Installation volume [m3] | 19
Arc including DFHA | 
Installation surface [m2] | 37
Access/manipulation surface [m2] | 41
Linear installation extension [m] | 35
Installation volume [m3] | 86

## Slide 30: Summary per IP
Maximum in surface |  |  |  | 
 | Crab cavities | Cryogenics | Cold Powering | Total
Installation area on surface | 2×172 m2 + 8 m2 | 1000 m2 | 2×450 m2 | 2244 m2
Installation area underground |  | 150 m2 |  | 150 m2
Maximum in tunnel |  |  |  | 
 | Crab cavities | Cryogenics | Cold Powering | Total
Installation area on surface | 2×65 m2 | 1000 m2 |  | 1130 m2
Installation area underground | 2×107 m2 + 8 m2 | 150 m2 | 2×450 m2 | 1280 m2
DFHA in RR |  |  |  | 
 | Crab cavities | Cryogenics | Cold Powering | Total
Installation area on surface | 2×172 m2 + 8 m2 | 1000 m2 | 2×372 m2 | 2096 m2
Installation area underground |  | 150 m2 | 2×88 m2 (RR) | 150+176 m2
DFHA + QDS in RR |  |  |  | 
 | Crab cavities | Cryogenics | Cold Powering | Total
Installation area on surface | 2×172 m2 + 8 m2 | 1000 m2 | 2×332 m2 | 2016 m2
Installation area underground |  | 150 m2 | 2×128 m2 (RR) | 150+256 m2

## Slide 31: Possible concepts of arrangements tunnel-surface

## Slide 32: Option A: long service tunnel
System | Sub-system | Location proposed | Building/structure
Crab cavity | RF power (2×IP) | Underground | Service Tunnel
 | LLRF racks (2×IP) | Underground | Service Tunnel
 | LLRF central racks | Underground | Service Tunnel Cryo
 | HVPS (2×IP) | Underground | Service Tunnel
Cryogenics | Warm compressor | Surface | Surface building Cryo
 | “SD” building | Surface | Surface building Cryo
 | Cold Compressor Box | Underground | Service Tunnel Cryo
Cold powering | DFHX (2×IP) | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHX PC ( 2×IP) | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHX QDS+QEE | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHM (2×IP) | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHM PC (2×IP) | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHX QDS+QEE | Surface/Underground | Sur. buildings CP/Service Tunnel
 | DFHA (2×IP) | Surface/Underground | Sur. buildings CP/RR Service Tunnel
 | DFHA PC (2×IP) | Surface/Underground | Sur. buildings CP/RR Service Tunnel
 | DFHX QDS+QEE | Surface/Underground | Sur. buildings CP/RR Service Tunnel

## Slide 33: Option A: long service tunnel
MACHINE
TUNNEL
NEW CORES FOR COAX CABLE TRANSPORT
SERVICE TUNNEL
EMERGENCY EXIT
A1
A2

## Slide 34: Option B: crab to the surface - B1 enlargement of an existing structure - B2: short service tunnel
System | Sub-system | Location proposed | Building/structure
Crab cavity | RF power (2×IP) | Surface | Crab service building Left and Right
 | LLRF racks (2×IP) | Surface | Crab service building Left and Right
 | LLRF central racks | Surface | Surface building Cryo+CP or specific building
 | HVPS (2×IP) | Surface | Crab service building Left and Right
Cryogenics | Warm compressor | Surface | Surface building Cryo
 | “SD” building | Surface | Surface building Cryo
 | Cold Compressor Box | Underground | Underground extension/ short service tunnel
Cold powering | DFHX (2×IP) | Surface | Surface building CP
 | DFHX PC ( 2×IP) | Surface | Surface building CP
 | DFHX QEE+QDS | Surface | Surface building CP+RR
 | DFHM (2×IP) | Surface | Surface building CP
 | DFHM PC (2×IP) | Surface | Surface building CP
 | DFHM QEE+QDS | Surface | Surface building CP+RR
 | DFHA (2×IP) | Underground | Surface building CP/RR
 | DFHA PC (2×IP) | Underground | Surface building CP/RR
 | DFHA QDS | Surface | Surface building CP/RR
Crab positions in lay-out blocked !!!!

## Slide 35
Option B1:
enlargement of existing tunnel
Enlargement of existing tunnel
Length_50m
(Top View)
USC55
UJ53
UJ57
RR53
RR57
USC55
Enlargement of existing tunnel
(Cross Section)
Enlargement of existing tunnel
(Frontal View)
USC55
UXC55

## Slide 36: From surface to tunnel for crab
Necessity to accommodate 8 coax. 270 mm diameter
From 1 to 8 ducts.
Exit in the tunnel in a new alcove or just on top of the cavities

## Slide 37: Option B2: short service tunnel

## Slide 38: Analysis building by building point by point

## Slide 39: Crab building
PERSONAL ACCESS
TRANSPORT ACCESS
CRAB CAVITY SURFACE BUILDING
(22.1 x 18.2 x 9 m3)
LLRF Racks
Slow Control
26.60 m2
16.72 m2
Drivers & Control
21.28 m2
9 m
18 m
22 m
IMPORTANT!!! The surface consider, it’s taking into account the space around the equipments.
So, it’s TOTAL surface
Partial underground building to reduce environmental impact (see later slides for positions)

## Slide 40: Crab building with some dimensions

## Slide 41
CP building, preliminary
DFHX (Power Converters): 55
DFHA (Power Converters): 38
DFHA (Spare Power Converters): 5
DFHM (Power Converters): 79
DFHX + DFHM (Spare Power Converters): 14
Cold Powering. Space Required. 316.5 m2 ( This for each IP side to be doubled)
DFHX
DFHM
DFHA

## Slide 42: Point 5

## Slide 43: POINT 5 Underground infrastructure
RR57
UJ57
UJ53
D2
Q4
Crab Module
*HL_LHC future integration of the Crab Module (152399 mm/IP) (Total length: 13400mm)
D2
Q4
Crab Module
LHC position;
D2_151930 mm from the IP
Q4_163350 mm from the IP
Crab Module position
152399 mm/IP
Total length: 13400 mm

## Slide 44
RR57
UJ53
D2
Q4
Crab Module
D2
Q4
Crab Module
LHC position;
D2_151930 mm from the IP
Q4_163350 mm from the IP
*HL_LHC future integration of the Crab Module (152399 mm/IP) (Total length: 13400mm)
POINT 5 Surface building
Crab Module position
152399 mm/IP
Total length: 13400 mm

## Slide 45
Point 5 option B2
CL+CR left
175m2 (10x17.5)
CL+CR RIGHT
175m2
New junction for RF
New junction for RF
2 cores dia 1.1m L 70m
2 cores dia 1.1m L 75m
Cold compressor
DFXJR
DFXJL
Surface buildings
Underground buildings (new or modified)
US54
Connection machine

## Slide 46
Warm Compressors cryo 600m2
“SD” cryo
300m2
LLRF central
PM54
Cold powering
1000m2 (25x40)
Point 5 option B2

## Slide 47
Warm Comp.
600m2
Cold powering
1000m2
CRYO SD
CRAB LSS5R
CRAB LSS5l

## Slide 48: Point 1

## Slide 49: POINT 1 Underground infrastructure
Crab Module position
152399 mm/IP
Total length: 13400 mm
D2
Q4
Crab Module
LHC position;
D2_151930 mm from the IP
Q4_163350 mm from the IP
*HL_LHC future integration of the Crab Module (152399 mm/IP) (Total length: 13400mm)
Crab Module
D2
Q4
Building 2160: “Station electrique”
RR13
UJ13
RR17
UJ17

## Slide 50
POINT 1 Surface building
D2
Q4
Crab Module
LHC position;
D2_151930 mm from the IP
Q4_163350 mm from the IP
*HL_LHC future integration of the Crab Module (152399 mm/IP) (Total length: 13400mm)
Crab Module
D2
Q4
Building 2160: “Station electrique”
RR13
UJ13
RR17
UJ17

## Slide 51
UJ13
UJ16
UJ14
UJ17
Pt2
Pt8
PM15 (9.1m)
PX14 (18m)
PX16 (12.6m)
PX15 (9.1m)
UX15
US15
USA15
Space reserved to
lower material
too small
PX14 et PX16 : fully used by experiments
POINT 1 : existing access points
PX15 (9.1m)
Construction SD 300m2 difficult
Space reserved to
lower material
Big enough
Can we enlarge the USA15 and build
connection tunnels ?

## Slide 52: PX15
The lowering and transport vertical space is still there ?
Can we use it ?

## Slide 53: If we can dream then … it could be something like this
PX15 (9.1m)
Warm Comp.
600m2
Cold powering
900m2
CRYO SD (300m2) no place near pit PX15
CRYO SD + new pit

## Slide 54
Cold
Powering
1000m2
SD “cryo” + pit 400m2
Wam compressor cyo 600m2

## Slide 55
Surface buildings and cores for Crab
LSS1R : impossible to drill core and build an other CE work directly up the crab
LSS1L : HT line in the area

## Slide 56: Option comparisons
 |  | Option A1 CP: service tunnel RF: service tunnel New pit | Option A2 CP: surface RF: service tunnel New pit |  | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension
 |  | SC link to the DFHA |  |  |  |  | No SC link to the DFHA | 
S | Central building CRY | 1000 m2 | 1000+900 m2 1900 m2 | 1000+900+8 m2 1908 m2 |  | 1000+900+8 m2 1908 m2 | 1000+644+8 m2 1652 m2 | 1000+280+8 m2 1288 m2
 |  | Cryo | Cryo + CP (X+M+A) | Cryo + CP (X+M+A) + LLRF |  | Cryo + CP (X+M+A) + LLRF | Cryo + CP (X+M) + LLRF | Cryo + CP (X+M) + LLRF
S | Crab buildings CL and CR |  |  | 175 m2 +175 m2 |  | 175 m2 +175 m2 | 175 m2 +175 m2 | 175 m2 +175 m2
U | Underground Extension |  |  |  |  | 150 m2 |  | 150 m2
 |  |  |  |  |  | plus connection to LHC machine |  | plus connection to LHC machine
U | RR |  |  |  |  |  | 2×128 m2 | 2×128 m2
U | Service Tunnel | 2×(175+ 450) + 8 + 150 m2 2×625+150 m2 | 2×(175) + 8 + 150 m2 2×175+150 m2 | 150 m2 |  |  | 150 m2 | 
 |  | RF+CP+LLRF+Cbox | RF + LLRF + Cbox | Cbox |  |  | Cbox | 
U | Vertical access | New PIT | New PIT | New PIT |  | PM54 New pit | New PIT | PM54 New pit

## Slide 57: Option comparisons I
 | Option A1 CP: service tunnel RF: service tunnel New pit | Option A2 CP: surface RF: service tunnel New pit | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension
 | SC link to the DFHA |  |  |  | No SC link to the DFHA | 
Access Crab | - | - | + | + | + | +
Access PC | - | + | + | + | + | +
Access QDS | - | + | + | + | + | +
Access QEE | - | + | + | + | + | +
Radio shielding PC | + | + | ++ | ++ | + | +
Radio shielding | + | + | + | + | + | +
Civil work impact on planning | Limited Connection to machine tunnel | Limited Connection to machine tunnel | Limited Crab connection | Important Common pit use | Limited Crab connection | Important Common pit use
Tunnel installation complexity | Very high | High | Mild | Mild | Easiest | Easy
Integration complexity | Difficult Cryo to SC link | Difficult Cryo to SC link | Mild | Mild | Easiest No SC link to DFBA | Easy No SC link to DFBA
Equipment simplification | Very high (only hor. SC link) | None | None | None | 4 SC link less probably the most complex to install and integrate no modif. of DFBA | 4 SC link less probably the most complex to install and integrate no modif. of DFBA

## Slide 58: Option comparisons II
 | Option A1 CP: service tunnel RF: service tunnel New pit | Option A2 CP: surface RF: service tunnel New pit | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension | Option B1 CP: surface RF: surface New pit | Option B2 CP: surface RF: surface Extension
 | SC link to the DFHA |  |  |  | No SC link to the DFHA | 
Extension of underground civil work | +++ | +++ | ++ | + | ++ | +
Service underground installation | ++++ | +++ | ++ | ++ | + | +

## Slide 59: Conclusions
Point 4: ready for detailed discussion and approval from HL-TC in order to go ahead with detailed studies (CRG), tendering pre-work (CRG) and 1st detailed activities list
Point 1 and point 5
  All needs have been collected and put together
    Cryo ok
    PC ok
    QDS and QEE 1st guess
    SC link: need of more information in particular taking into account DFHM (see PLC where we approved the lay-out)
  Various options have been looked at putting in evidence pro and cons
Next steps
  Define baseline
  Perform feasibility, technical and cost estimation by CE. The present presentation shall be taken as base document to start the analysis work.
  Improve installation studies by the concerned WP in the order
    CRG
    SC link
    Crab cavities
  Add services to the analysis

## Slide 60: END