## Slide 1: Semiconductor Switch Designs
M.J. Barnes
Acknowledgements
W. Bartmann, L. Ducimetière, B. Goddard,
J. Holma, A. Lechner, T. Fowler, T. Kramer,
M. Meddahi, R. Schmidt
FCC week, 23th-27th March 2015

## Slide 2: Outline
Requirements for FCC injection kickers;
An existing kicker system at CERN;
The need for developments of semiconductor (solid-state) switches;
Possible semiconductor switch topologies for injection;
Requirements for FCC extraction (dump) kickers;
Possible semiconductor switch topologies for extraction;
Other R&D required;
Timeline and tasks for R&D;
Summary.

## Slide 3
FCC injection kicker system requirements |  | 
 |  | FCC Injection
Magnet technology |  | Delay line
Kinetic Energy | TeV | 3.3
Kick | mrad | 0.29
B.dl | T.m | 3.2
Aperture height | mm | 18 + 17 = 35
Aperture width | mm | 18 + 17 = 35
Field rise/fall time | µs | 0.28
Field flattop length | µs | 2.25
Field flattop ripple | % | ±0.5
System impedance | Ω | 5
Assumed system magnetic length | m | ~30
Magnet current | kA | ~0.31 to ~3.1
Pulse voltage range | kV | 1.8 to 18
Approximate number of injection kicker systems |  | 40

## Slide 4: An existing kicker system at CERN
In general, line type modulators are used with a main switch and a dump switch;
  switch is typically a thyratron (closing switch);
Impedance matched Pulse Forming Line/Network (PFL/PFN), to minimise reflections, but requires the PFL/PFN to be charged to twice the load voltage;
PFL is probably most appropriate for FCC injection.
LHC Injection PFN
Line Type Modulator:
Max. pulse length = 2τp
I

## Slide 5: The need for new developments
Thyratrons:
  pre-fire (self turn-on without a trigger signal) is a concern;
  long-term availability is a real concern;
  have limitations with regard to dynamic range and repetition rate;
  is only a closing switch  need for PFN/PFL for energy storage.
Pulse Forming Line:
PFL has limitations: it should be matched to the load impedance, but coaxial transmission lines are commercially available only with certain impedances;
It is increasingly difficult to source coaxial transmission line for the highest voltage (~80 kV) kicker systems.
Suitable semiconductor switch topologies can help to solve the above problems.
CERN PS PFLs
Injected beam
Circulating beam
Internal dump
Kicker magnet
Require a reliable kicker system, for
FCC, to avoid mis-kicking beam:
BUT….
Unkicked inj.
Kicked circ.

## Slide 6: Semiconductor Switches
Generally reliable and are not prone to self-triggering;
Allow a wide dynamic range of operation;
Maintenance is significantly reduced compared to gas switches;
Series and parallel connection of power semiconductor switches can potentially achieve designs with very high pulse power.
Examples of suitable switch technologies are:
  Marx Generator;
  Inductive Adder;
Depending upon the switch technology, solid-state modulators can be opened when conducting full load current, hence;
  only a portion of the stored energy is delivered to the load during the pulse (therefore a PFL or PFN is not required);
  potentially limit fault current in the event of a magnet (load) electrical breakdown;
  source impedance can be low, hence source voltage does not need to be doubled.

## Slide 7: FCC Injection: Marx Generator
Low source impedance;
No output transformer  maximum pulse length limited by capacitor values and load;
Modularity: same design can be used for different voltage (and current) specifications;
Switches and control electronics are not referenced to ground;
An international collaboration has been proposed between CERN and ISEL, Portugal, to investigate Marx Generators as a potential replacement for thyratrons (in existing systems at CERN too).
Operation: Capacitors charged in parallel (shown: even # switches on), and discharged in series (odd # switches on)
 high voltage output.

## Slide 8: FCC Injection: Inductive Adder
Adder originally developed at SLAC/LLNL;
Extremely high precision prototype built at CERN, for CLIC, based on MOSFETs (fast switching).
Modularity: the same design can be used for different voltage and current specifications;
Short rise time can be achieved (< 10 ns);
Potentially interesting for consolidation
of existing (short pulse) systems too;
Switches and control electronics are referenced to ground;
Promising technology for FCC injection;
Output pulse voltage can be modulated;
Redundancy easy to build-in;
Output transformer  maximum pulse length limited to typically ~3 μs;
(N-1)
layers
Leakage inductance
Capacitors
Primary loop inductance
Fast diode clamp
Magnetizing inductance
Semiconductor switches
Trigger
Trigger
Constant Voltage Layers
Analogue Modulation Layer
Load
Gate drive circuit
Gate drive circuits
1:1 coaxial transformer
Primary current
Semiconductor switch (x8)
Capacitor (x8)
5 layer CLIC prototype

## Slide 9
FCC extraction kicker system requirements |  | 
 |  | FCC Extraction
Magnet technology |  | Lumped inductance
Kinetic Energy | TeV | 3.3 to 50
Kick | mrad | 0.15
B.dl | T.m | 1.6 to 25
Aperture height | mm | 36
Aperture width | mm | 36
Field rise/fall time | µs | ≤3
Field flattop length | µs | 350
Field flattop ripple | % | 10
System impedance | Ω | 
Assumed system magnetic length | m | ~90
Magnet current | kA·Turns | ~0.55 to ~8.3
Output pulse voltage range | kV | 
Approximate number of extraction kicker systems |  | 300

## Slide 10: Existing LHC Extraction System
  Generator voltage must track the beam energy and have a low pre-fire rate.
Gate Turn-Off Thyristor’s, modified to be fast turn-on devices, are connected in series  high di/dt;
Allows a wide dynamic range of operation;
Fourteen extraction kicker systems per beam:
  for safety reasons, in case of pre-fire of one generator, all are triggered  asynchronous dump.
Two parallel generators (redundancy).
Voltage: 2.2kV – 30kV;
Current: 1.3kA – 18.5kA;
Current flat top: 95μs.
LHC dump – beam sweep:

## Slide 11
FCC Extraction System
System must be ULTRA RELIABLE
Consider an highly segmented system:
  hence pre-fire of one generator does unduly influence beam;
  not necessary to trigger other generators  doesn’t give an asynchronous dump;
  redundancy..
Several switch topologies under investigation:
  Scale existing LHC extraction generator for FCC (for segmented system  reduced current compared to LHC generator);
  Brainstorming  idea based on an opening semiconductor switch:
    switch is normally closed (conducting current) during inj. and ramp;
    switch opened to switch off current and extract beam;
    current proportional to kinetic energy of beam;
    “fail safe” (no current  beam extracted);
    BUT high losses, maybe superconductivity can be used???
Talk by W. Bartmann (Tuesday)

## Slide 12: Other R&D Required (Inj. & Ext.)
Study performance of various semiconductors, e.g. SiC, MOSFETS, IGBTs, …. (now & 10-20 years time???);
Magnetic materials;
Ultra reliable triggering/controls;
Other ideas for switch topologies;
Failure mode analysis;
Redundancy;
Fault tolerance;
Reliability;
Possibility of locating generator in tunnel, under magnet;
  Shielding of electronics;
  Radiation tolerant components;
Low source impedance may result in high fault current;
  Controls must detect fault current and limit magnitude;
Triggering method(s), e.g. fibre optics;
…….

## Slide 13: Timeline and tasks
2015:
Task 1: Complete proposal (objectives, timeline, identify lab space, secure resources, secure budget, and establish formal collaborations).
Task 2: Study overall concepts and kicker system options, and define key parameters for FCC injection and/or extraction kicker generators.
2016 - 2017:
  Task 3: Test and select individual components (switches and magnetic materials for cores), design of the prototype for FCC injection. [collaborations sought]
2018:
  Task 4: Document results and CDR write-up.
  Task 5: Construct the prototype system (generator, transmission lines, load).
2019:
  Task 6: Test the prototype.
Note: timeline is dependent upon resources and budget availability…..
Collaborations very welcome!

## Slide 14: Summary
Very challenging requirements;
High reliability kicker systems are required for FCC;
Parallel and series arrays of semiconductor switches are promising for both FCC and consolidation of existing kicker systems;
  eliminate pre-fire associated with thyratrons;
  eliminate need for very high voltage rating coaxial cable;
  built in redundancy;
  modularity.
Closing and opening capability eliminates the need for a PFL/PFN;
  Source impedance can be low, allowing a relatively small number of series connected power semiconductors. BUT requires a careful consideration of fault conditions;
Redundancy, fault tolerance, radiation tolerance,…

## Slide 15: Thank you for your attention!
Comments and suggestions are VERY welcome.

## Slide 16: Spare Slides

## Slide 17: Line type modulator example waveforms

## Slide 18
0
-2k
-4k
-6k
-8k
2k
0
1μs
2μs
3μs
4μs
5μs
Simulation:
Magnet current
Switch voltage
FCC Extraction System: opening switch possibility

## Slide 19: Example of normal and fault currents